## Summary
2020-2022
Table | Activity | Initiative | Risk Reduction | Spend ('000 in 2019 dollars) | RSE
23 - Grid design and system hardening | 2.7 | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault: circuit breaker relay hardware for fast curve (SH-6) | 0.209 | 24840.589 | 8.4138
23 - Grid design and system hardening | 3.1 | Covered conductor installation: covered conductor (SH-1) | 41.5686 | 1776408.1887 | 23.4004
23 - Grid design and system hardening | 6.1 | Distribution pole replacement and reinforcement, including with composite poles: composite poles and crossarms (SH-3) | 0.66175 | 178030.3667 | 3.7171
23 - Grid design and system hardening | 6.2 | Distribution pole replacement and reinforcement, including with composite poles: deteriorated pole | 0.067452 | 19594.0192 | 3.4425
23 - Grid design and system hardening | 7 | Expulsion fuse replacement: Branch line protection strategy (SH-4) | 0.1699 | 18679.3749 | 9.0958
23 - Grid design and system hardening | 9 | Installation of system automation equipment: installation of system automation equipment - remote controlled automatic reclosers settings update (SH-5) | 0.016049 | 8319.5136 | 1.929
23 - Grid design and system hardening | 16 | Undergrounding of electric lines and/or equipment: undergrounding overhead conductor (SH-2) | 0.28267 | 59500 | 4.7508
24 - Asset management and inspections | 4 | Infrared inspections of distribution electric lines and equipment: infrared inspection of energized overhead distribution facilities and equipment (IN-3) | 0.0058771 | 1175.85 | 4.9982
24 - Asset management and inspections | 5 | Infrared inspections of transmission electric lines and equipment: infrared inspection, corona scanning, and high definition imagery of energized overhead transmission facilities and equipment (IN-4) | 0.0058323 | 10323.5475 | 0.56495
24 - Asset management and inspections | 9.1 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations: distribution high fire risk-informed inspections (IN-1.1) | 6.8159 | 320323.2709 | 21.2781
24 - Asset management and inspections | 9.2 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations: aerial inspections (IN-6.1) | 4.7506 | 293273.8007 | 16.1986
24 - Asset management and inspections | 10.1 | Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations: transmission risk-informed inspections in HFRA (IN-1.2) | 1.3191 | 76571.2129 | 17.2275
24 - Asset management and inspections | 10.2 | Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations: aerial inspections - transmission (IN-6.2) | 0.82904 | 52608.3716 | 15.7586
25 - Vegetation management and inspections | 5.1 | Fuel management and reduction of “slash” from vegetation management activities: expanded pole brushing (VM-2) | 0.71373 | 12196.8708 | 58.5174
25 - Vegetation management and inspections | 16.1 | Removal and remediation of trees with strike potential to electric lines and equipment: hazard tree (VM-1) | 4.4347 | 179067.2279 | 24.7655
25 - Vegetation management and inspections | 16.2 | Removal and remediation of trees with strike potential to electric lines and equipment: DRI quarterly inspections and tree removals (VM-4) | 3.3699 | 111008.475 | 30.3574
26 - Grid operations and protocols | 5 | PSPS events and mitigation of PSPS impacts | 8.2792 | 147118.6647 | 56.2758