## Tree Risk Model
Impact Strike Score (ISS) |  |  |  | Tree Risk Heat Map
Description | Selection | Score | /Possible | 1 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | P1
Voltage Impact (VI) | Aerial cable | 0 | /10 | 2 | 12 | 22 | 32 | 42 | 52 | 62 | 72 | 82 | 92 | P2
Fire Impact (FI) | Non-HFTD | 0 | /10 | 3 | 13 | 23 | 33 | 43 | 53 | 63 | 73 | 83 | 93 | P3
Likelihood of Impact (LI) | Somewhat Likely | 0 | /5 | 4 | 14 | 24 | 34 | 44 | 54 | 64 | 74 | 84 | 94
|  |  |  | 5 | 15 | 25 | 35 | 45 | 55 | 65 | 75 | 85 | 95 | P2 | 50 - 63 | Within 90 days
|  |  |  | 6 | 16 | 26 | 36 | 46 | 56 | 66 | 76 | 86 | 96 | P2 | 64 - 79 | Within 60 days
Likelihood of Failure (LoF) |  |  |  | 7 | 17 | 27 | 37 | 47 | 57 | 67 | 77 | 87 | 97 | P2 | 80 - 100 | Within 30 days
Description | Selection | Score | /Possible | 8 | 18 | 28 | 38 | 48 | 58 | 68 | 78 | 88 | 98
Tree Lean (TL) | Slight or No Lean (<7 degree lean) | 0 | /10 | 9 | 19 | 29 | 39 | 49 | 59 | 69 | 79 | 89 | 99
Tree Height Factor (THF) | RCD-1.0x | 1 | /8 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Site Condition Attributes (SCA) | No Impact | 0 | /7
Overall Tree Condition (OTC) | No defects | 0 | /50
Risk Response
| ISS | 0
| LoF | 1
| Risk Rank Score (RRS) | 1
| Priority Rating | P3 | subject tree

## Likelihood of Failure (LoF)
Tree Lean (TL) | Score | Selected Value (SV)= SUM(CHOICEVALUES(TD))
Slight or No Lean (<7 degree lean) | 0
Moderate Lean (8-25 degree lean) | 5 | Selected Impact (SI)= | IF (SV < 15), then 0
Heavy Lean (25+ degree lean) | 10 |  | ELSE IF (15 < SV < 30), then 15
ELSE IF (30 < SV < 50), then 30
Tree Height Factor (THF) | Score |  | ELSE IF (SV ≥ 50), then 50
RCD-1.0x | 1
1.1x-1.4x | 3
1.5x-2.0x | 5 | Defect Impact (DI)= | IF (SI > OTC), then SI
2.0x+ | 8 |  | ELSE IF(OTC ≥ SI), then OTC
Site Condition Attributes (SCA) | Score | Likelihood of Failure score (LoF)=TL + THF + SCA + DI
No Impact | 0
High stand density with single species composition | 1 | Highest possible impact= 75
Change in drainage | 2
History of repeated outages on circuit (evidence of splicing) | 2
Areas known to be affected by introduced tree pathogens (Bark Beetle) | 3
Change in grade | 3
Fire damage | 3
Cultural disturbance to landscape - natural or unnatural | 3
Construction – including trenching, paving or road construction | 4
Areas of recent clearing/thinning/logging/new edge | 5
Soils prone to slides | 5
High winds | 7
Overall Tree Condition (OTC) | Score
No defects | 0
Minor defects (small codom top, nuisance insect/mistletoe infestation, unfavorable species) | 15
Moderate defects (moderate rot, epicormic sprouts, large codom top, multiple trunks, severe insect/mistletoe infestation, early stages of serious disease, exposed roots, some minor or moderate defects that have an additive effect) | 30
Major defects (crack in trunk, prevalent rot, history of branch/trunk failure, codominant, prevalent signs of serious disease, several minor and/or moderate defects) | 50
Tree has failed, uprooted, or is currently failing/uprooting and requires immediate attention | No Score, P1 Only
Tree Defects (TD) | Score
Small codom top (top 1/4 of tree height) | 1
Moderate codom top (1/2-3/4 of tree height) | 3
Large codom top (1/4 to 1/2 tree height) | 7
Multiple trunks, very low codom (bottom 1/4 of tree height) | 10
Nuisance insect or mistletoe | 1
Moderate insect or mistletoe | 10
Severe insect or mistletoe infestation | 20
Dead branches/dead top | 5
Dieback of twigs or branches | 10
Fungal fruiting bodies | 15
Minor rot | 5
Moderate rot | 20
Prevelant rot | 35
Major rot | 50
Minor included Bark | 10
Major included Bark | 25
Poor Pruning Practices | 1
Weak, unsound branch attachments | 10
Species prone to failure | 10
Early stages of serious disease | 10
Prevelant signs of serious disease | 30
Epicormic sprouts | 1
Minor exposed or girdling roots (<25%) | 5
Moderate exposed or girdling roots (25-50%) | 20
Serious exposed or girdling roots (>50%) | 40
Crack in trunk | 20
Major cracks | 50
Seams/ribs | 5
History of branch failure | 10
History of trunk failure | 20
Tree dead | 50
Basal wound | 5
Bleeding/resinous | 1
Live crown ratio <50% | 20
Structurally unsound trunk/poor taper | 5

## Impact Strike Score (ISS)
Voltage Impact (VI) | Score | Impact Strike Score (ISS)= VI + FI + LI
Aerial cable | 0
<2.4kV (service, secondary, guy wire) | 2 | Highest possible impact= 25
2.4-21kV (distribution) | 4
33-66kV (subtransmission) | 6
115-220kV (transmission) | 8
500kV (transmission) | 10
Fire Impact (FI) | Score
HFTD | 10
Non-HFTD | 0
Likelihood of Impact (LI) | Score
Unlikely | -5
Somewhat Likely | 0
Likely | 5
Very Likely | 5