## Slide 1: Covered Conductor Inspection: Results and Next Steps
AES - Linear Asset Engineering
March 26, 2020
Document updates history:
3/11/2020 removed Client Privilege after review with Law – This is operational issue.
3/26/2020 reformat to present data and recommendation succinctly
6/15/2020 – meeting notes with B. Scholler and team updates on completed action items

## Slide 2: Objectives
The objectives of the presentation are to 1) bring-forth the findings of covered conductor inspection, 2) seek support for the proposed plan to improve the gaps found from the inspection findings, and 3) provide recommendation to continue inspection on all covered conductor installation to date

## Slide 3: Executive Summary
Linear Asset Engineering conducted a sampled inspection program to validate that installation of covered conductor is conforming to the new SCE Standards supporting Wildfire Mitigation Plan (WMP)
This validation activity was in addition to normal QC of covered conductor spans and poles
The sampled inspection program identified approximately 30% of recent covered conductor installation not conforming to the new standards supporting Wildfire Mitigation
  The six issues identified were: 1) missing lightning arresters, 2) excessive angle, 3) over-tensioned conductor, 4) wrong jumper wire utilized, 5) missing wildlife covers (the bulk of the issues), and 6) partially exposed conductor
Construction issues are most likely due to the lack of understanding of the new standards and possibly gaps in process that prevented proper use equipment and tools.
In addition, a few field failure reports have identified root causes, which are in-line with construction issues found during sampling inspection.
We recommend taking the following actions:
  Reinforce SCE standards on wildfire mitigation by issuing Operating Bulletins, presenting to wildfire information summit, and holding re-training sessions
  Issue “go-back” fixes to correct construction and bring up to SCE standards
  Incorporate findings into inspection programs (EOI, AOI, and QC) to reinforce standards
  Reformat the Distribution Design Standards to create a dedicated wildfire mitigation section
  Recommend that all covered conductor installed to date be inspected for compliance to Design and Construction Standard (approximately 450 miles remaining) – cost impact $2.75 M (contractors), or 5 full time inspectors + $250k (SCE resources)
Next Steps
  Meet with DBL senior leadership team to discuss findings and seek alignment on recommendation
  Present at FSC to seek approval to continue inspection

## Slide 4: Action Item Updates

## Slide 5: Identified three-pronged approach for addressing covered conductor installation issues
Linear Asset Engineering conducted a sampled inspection program to validate that installation of covered conductor is conforming to the new SCE Standards supporting Wildfire Mitigation Plan (WMP)
The sampled inspection program identified approximately 17% of recent covered conductor installation not conforming to the new standards supporting Wildfire Mitigation
  The six issues identified were: 1) missing lightning arresters, 2) excessive angle, 3) over-tensioned conductor, 4) wrong jumper wire utilized, 5) missing wildlife covers (the bulk of the issues), and 6) partially exposed conductor
With this inspection result, we developed three overall approaches:
  Standards - we need to develop sets of mitigation on changing the behaviors, practices to avert these issues for new installation of covered conductor. This includes multiple methods of communications to effectively enforce correct implementation of standards.
  Inspection - how we go about to leverage the inspected data to make adjustments of current inspection programs to identify and fix these identified issues
  Risk Mitigation - the found issues might create some risks or rather reduce risk buy-down of covered conductor mitigation. We want to leverage the inspection results to develop mitigation to reduce this risk or rather increase the risk buy-down.
Notes: Notes captured on 6/22/2020
This validation activity was in addition to normal QC of covered conductor spans and poles

## Slide 6: Standards and Communication
Standard Updates
  The DOH Standard updates will be published during the Q3 Cycle (July 2020)
    Updates Include
      Clarification of wildlife cover requirements for covered conductor systems
      Clarification of jumper requirements for covered conductor systems
      Clarification of PGW ampacity and conductor data
  The DDS Standard will be updated to improve flow of overall wildfire mitigation requirements will be published on August 2020
  A Standard Information Summit will be held to communicate the standard updates
Operating Bulletin
  Bulletins targeting field personnel regarding the following have been published
    Reinforcement of sag and tension requirements for covered conductor
    Reinforcement of proper stripping methods to prevent conductor damage
Design Support Notes (DSN)
  Design Support Notes targeting the planning organization will be published on July 2 and details the following
    Lightning arrester requirements for covered conductor systems
    Limiting angle requirements for covered conductor systems
Contractor Retraining
  Inspection findings will be shared all Regional Construction Managers or their representative in Ad-Hoc information session

## Slide 7: Leverage Existing Inspection Programs
The CC inspection results were shared with the following inspection programs
  Quality Control
  Overhead Detail Inspections
  Aerial Detail Inspections
Further Developments
  Plan to develop set of questions focused on the 6 main issues for covered conductor systems to include in ODI and ADI
    ODI modified checklist to include check for covered conductor and if covers are installed
    ADI Inspections already include check on wildlife cover requirements, and if there are equipment
    Gaps for all programs are the ability to check for over-tensioned and excessive angle on x-arm
Construction Oversight for Contractors
  Due to resource constraint, there is no set process or requirement for oversight on contractor construction work
Will continue to seek opportunity to socialize standard updates that may impact inspection and any additional findings

## Slide 8: Risk Mitigation– Stage Gate
Determine process to create notifications and timeline for mitigating 405 FLOCs
  Will focus on prioritizing high risk items such as over-tension in high loading areas (12) and excessive angle (51)
Options for inspection and fixes for remaining cover conductor installations:
  Repurpose the engineering inspection check list to focus only inspection of each FLOC on six types of issues. This could be done by SCE or contractor
  Leverage ODI/ADI to inspect these six issues over the inspection cycle
    Will meet with Ray to understand differences and review existing checklists
    Need process to create notifications for items found

## Slide 9: Inspection Results

## Slide 10: Inspections identified ~17% of pole/line construction does not conform to SCE Standards for WFM
Approx. poles (circuit miles) with CC installed by Jan 2020: 12,552 (523 circuit miles)
Poles inspected by field inspectors: 3435 (~140 circuit miles)
Poles reviewed/validated by engineers: 3435 (as of 8/5/2020)
  Poles with potential issues are marked by inspector. Existence of issue is validated by engineering.
1. Note that a structure may have more than one issue
Chart: Summary of Results
| Wrong Insulator | Missing Equipment Bushing Cover | Missing Pothead Cover | Missing Lightning Arrester Cover | Over-tensioned | Incorrect Wildlife Cover Install | PGW Jumper | Excessive Angle | Partially exposed conductor | Missing Lightning Arrester on Equipment Pole | Missing Fuse Covers | Missing Connector Covers | Missing Dead-end Covers
High | 1 | 1 | 1 | 4 | 15 | 25 | 34 | 57 | 72 | 115 | 124 | 131 | 240
P3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P2 | 0 | 0 | 0 | 0
Findings from pole and line inspection
Chart: Results: Structure Level1
| No Issues Found | Issues found
 | 2848 | 587

## Slide 11: Six construction issues were identified as non-conforming to SCE Standards and possible risks
Construction Issue | SCE Standard Requirements | Possible Risks of Nonconformance to Standard
1. Missing Lightning Arrester on Equipment Pole | Lightning arresters must be installed on equipment poles on covered conductor systems. | Covered conductor burn down during fault at transition point (cover to bare) if lightning arresters are absent.
2. Excessive Angle | The line angle must not exceed the critical crossarm angle limits per the table in SCE’s standards. Apply the appropriate crossarm construction (i.e. double crossarm or double dead-ends) to reduce the mechanical stress. | Excessive angle leads to mechanical stress on crossarms and insulators, resulting in wire down.
3. Over-tensioned conductor | Must follow the correct methods and the new sag/tension tables for covered conductor as shown on the standards | Over-tensioned covered conductor span may result in broken and wire down.
4. Wrong Material Used (Insulator and Jumper) | Must use polymer insulators with covered conductor Must use the same covered conductor size for jumper wires | The use of wrong materials, such as porcelain insulators and jumper wires, may lead to a failure. Porcelain insulators will cause tracking on the covering, allowing it to deteriorate. Using PGW as a jumper may lead to a burn down due its lower ampacity rating.
5. Missing Wildlife Covers Note 1 | Appropriate wildlife covers must be installed for Dead-end, Connector, Fuse, Lightning arrester, Equipment Bushing, Pothead | Absence of wildlife covers reduce the effectiveness of covered conductor installation and may result in contact-related faults
6. Partially exposed conductor | Any exposed conductor must be covered. For example: exposed parts of conductors at dead-ends, connectors, splices must be covered with the appropriate covers as specified in the standards. | Exposed conductor may reduce the effectiveness of covered conductor.
Note 1: Missing wildlife covers are separated into distinct issues in Summary of Results chart on slide 4

## Slide 12: Improvement Opportunities

## Slide 13: Summary of Improvement Opportunities
Five improvement opportunities were identified based on inspection results
  Reinforce SCE standards on wildfire mitigation by issuing Operating Bulletins, presenting to wildfire information summit, and holding re-training sessions
  Issue “go-back” fixes to correct construction and bring up to SCE standards
  Incorporate findings into inspection programs (EOI, AOI, and QC) to reinforce standards
  Reformat the Distribution Design Standards to create a dedicated wildfire mitigation section
  Recommend that all covered conductor installed to date be inspected for compliance to Design and Construction Standard (approximately 450 miles remaining) – cost impact $2.75 M (contractors), or 5 full time inspectors + $250k (SCE resources)

## Slide 14
Action | Owner | Target Date | Status
Publish bulletin reinforcing importance of correct sags and tension for construction personnel | Linear Asset Eng. | 3/9/2020 | Completed
Publish bulletin focused on proper stripping methods and tools for construction personnel | Linear Asset Eng. | 4/15/2020 | Completed
Publish bulletin reinforcing standard requirements for crossarm angle limits for planning and construction personnel | Linear Asset Eng. | 4/30/2020 | In Progress. Scheduled to publish on July 2
Publish bulletin reinforcing lightning arrester requirements for planning and construction personnel | Linear Asset Eng | 4/30/2020 | In Progress. Scheduled to publish on July 2
Present findings and reinforce requirements at the Wildfire Information Summit | Linear Asset Eng | 4/2020 & 5/2020 | Event repurposed to quarterly standards info. summit in August 2020
Hold re-training sessions on proper installation of covered conductor | Technology Integration | 5/30/2020 note 1 | In Progress. Target date subject to change per note.
Update standard to clarify jumper requirements and wildlife cover requirements | Linear Asset Eng. | 7/31/2020 | On Target. Scheduled to publish July 2020
Improvement Opportunity #1: Reinforce Standards
Reinforce SCE standards on wildfire mitigation by issuing Operating Bulletins, presenting to wildfire information summit, holding re-training sessions, and update standards for clarification
Note 1: Target date need to be confirmed by impacted owner, and may change

## Slide 15: Improvement Opportunity #2: Issue “Go-back” Fixes
Action | Owner | Target Date | Status
Communicate findings with Quality Control team | Linear Asset Eng. | 2/28/20 | Completed
Work with QC and DBL team to create a mechanism for issuing remediation notifications for issues found | QC, DBL, and Linear Asset Eng. (see note 1) | 4/15/2020 | Target date to change per note
Issue remediation notifications for issues identified during inspection | DBL (see note 1, 2, 3) | 5/30/2020 | Target date to change per note
Note:
1) Target date need to be confirmed by impacted owner, and may change
2) Distribution Business Line is identified as owner of the fixes at this time, but Linear Asset Engineering will need to work with DBL to establish a process
3) Cost responsibility is unknown at this time since inspection did not capture if work was performed internally or by contractor, and if by contractor, whether the work order map was correctly followed
Issue “go-back” fixes for 50 miles already inspected to correct construction and bring up to SCE standards
Create process for inspection and issuance of remediation of remaining 475 miles (see recommendation on “Next Steps”)

## Slide 16: Improvement Opportunity #3: Incorporate findings to existing inspection programs
Action | Owner | Target Date | Status
Communicate findings with ground based and aerial based inspections | Linear Asset Eng. | 4/30/2020 | Complete
Work with EOI and AOI team to incorporate findings into survey for future inspections | Linear Asset Eng., Asset Assessment and Data Strategy, and Regulatory Affairs and Compliance note 1 | 5/15/2020 | Complete
Incorporate findings into inspection surveys | Asset Assessment and Data Strategy, and Regulatory Affairs and Compliance note 1 | 5/30/2020 | Impacted Owner to confirm completion
Incorporate findings into inspection programs (Ground Inspections, Aerial Inspections, and Quality Control) to reinforce standards
Note 1: Target date need to be confirmed by impacted owner, and may change

## Slide 17: Improvement Opportunity #4: Update Distribution Design Standard
Action | Owner | Target Date | Status
Create a dedicated wildfire mitigation section in the Distribution Design Standard (DDS) | T/D Standards and Tech Transfer | 7/31/2020 | On Track
Reformat the Distribution Design Standards to create a dedicated wildfire mitigation section

## Slide 18: Improvement Opportunity #5: Expand Covered Conductor Inspections
Recommend that all covered conductor installed to date be inspected for Standard compliance for the following reasons
  Extensive issues found (almost 30% of poles inspected) so far
  Initial circuits are in HFRA and prioritized first
Recommend continuing to use Engineering contractor for inspection of remaining 475 miles since inspection checklists and tools have been refined (use this effort to operationalized inspection of CC for future construction in HFRA)
  Work could be transitioned to other internal organization (i.e. DBL or QC) if desired, and will need transition time
  Engineering Contractor Option: Anticipated cost for continued inspection is $2.5 M, assuming 5 inspectors working full time
  SCE Internal Option: Need 1 month set-up time with internal resources and 5 full time inspectors for 1 year
  Both options will have an anticipated cost for utilization of inspection tools and data capture around $250 K
Action | Owner | Target Date | Status
Expand inspection scope to include remaining 475 circuit miles of covered conductor note 1 | Linear Asset Eng. | 6/1/2020 | In progress. Awaiting final approval for project.
Complete inspection of all 523 circuit miles note 1 | Linear Asset Eng. | 5/30/2021 | In progress
Note 1: Target date need to be confirmed by impacted owner, and may change

## Slide 19: Next Steps

## Slide 20: Next Steps
Action | Owner | Target Date | Status
Meet with stakeholders (DBL Senior Leadership Team) to determine appropriateness of recommendation, and organization to execute the work | Linear Asset Eng. | 4/15/2020 | In Progress
Provide recommendation to FSC and seek approval to continue inspection | AES | 5/15/2020 | In Progress
Note 1: Effort is assuming DBL SLT and FSC agree with and approve recommendation

## Slide 21: Detailed Recommendations on “Go Back” Fixes

## Slide 22: Recommended actions for correcting already installed and ensure no repeating non-conformance for new construction of covered conductor
Issue | Existing Construction | New Construction
Structures missing Lightning Arrester on Equipment Pole | Install lightning arresters on equipment poles that currently do not meet the DOH Construction Standard | Reinforce DOH Standard requirement through bulletins for planning and construction personnel. Partner with tech planning to ensure that planning is aware of bulletin and requirements are followed.
Excessive Angle | Reconstruct structure to meet line angle guidelines in the DOH and DDS | Reinforce DOH Standard requirement through bulletins for planning and construction personnel. Partner with tech planning to ensure that planning is aware of bulletin and requirements are followed.
Over-tensioned conductor | Verify the span’s tension. Once confirmed, remediate by re-sagging or reconductoring the over-tensioned span. | Reinforce DOH Standard requirement through bulletin for construction personnel. Work with construction methods and technology integration to ensure that the proper tools are provided.
PGW Jumper | Replace PGW with appropriately sized covered conductor | Reinforce DOH Standard requirement through bulletin for construction personnel. Update standard to provide ampacity of PGW and be more prescriptive on appropriate PGW installation.
Missing Wildlife Covers | Install wildlife cover on equipment and hardware that do not have them | Update standard to be more prescriptive on wildlife cover requirements. Work with supply chain to ensure that enough material is on hand.
Partially exposed conductor | Cover exposed area with split tube | Update standard to require exposed conductor at dead-ends to be covered with split tube

## Slide 23: Recommending priority for correcting installed covered conductor based on risk assessment
Issue | Risk | Recommended Priority
Structures missing Lightning Arrester on Equipment Pole | Overvoltage conditions that lead to arcing may cause failure if the arc travels to a bare to covered transition point. Once the arc meets the covered portion, the arc stops, causing the conductor to melt and burn down. | High
Excessive Angle | Excessive deviation angles will mechanically overtax the insulator or crossarm, leading to their failure. | High
Over-tensioned conductor | Over-tensioning the lines will mechanically stress the conductor, conductor support, and structure. It will also make the conductor more susceptible to Aeolian vibration. This will lead to premature failure of the covered conductor. | High
Missing Dead-end Covers | Exposed conductor is present at dead-ends. The increased length of exposed present at dead-ends leads to an increased contact with wildlife or vegetation risk and possible failure at the bare to covered transition point when arcing occurs. Dead-end covers minimize these risks. | High
PGW Jumper | PGW jumpers have a lower current carrying capacity than 1/0 ACSR or #2 Copper. Therefore, they will act as a fuse on the line when using them as jumpers. | High
Wrong Insulator | Using porcelain insulators with covered conductor will cause tracking on the covering. Tracking will erode the covering, making it lose its effectiveness. | High
Missing Connector Covers | Exposed conductor is present at connection points, leading to contact with object risk and possible failure at the bare to covered transition point when arcing occurs. Connector covers minimize the risk. | Medium
Partially exposed conductor | Exposed conductor may lead to contact with object risk and possible failure at the bare to covered transition point when arcing occurs. | Medium
Missing Fuse Covers | Exposed connections points on the fuse may lead to phase-to-phase or phase-to-ground contact. Single phase configuration will have a lower risk of phase-to-phase contact compared to three phase configuration due to spacing. | Low
Missing Lightning Arrester Cover | Exposed connections points on the lightning arrester may lead to phase-to-phase or phase-to-ground contact. | Low
Missing Equipment Bushing Cover | Exposed connections points on the equipment arrester may lead to phase-to-phase or phase-to-ground contact. | Low
Missing Pothead Cover | Exposed connections points on the pothead may lead to phase-to-phase or phase-to-ground contact. | Low
Note: Various missing covers have different priority levels due to the amount of exposed conductor, for example a missing dead-end cover will expose a larger area of bare conductor compared to a missing connector cover

## Slide 24: Priority Timeline
Priority | Recommended Remediation Timeline | Reason
High | 6 months (P2 equivalent) | These issues pose the highest failure risk necessitating prompt action. High winds and ice loading may exacerbate some of the issues, making remediation before fall (high winds) and winter (ice) prudent.
Medium | 18 months | These issues introduce some contact with object risk. It is prudent to remediate these issues to prevent possible ignition, however the urgency is moderate because the amount of exposed conductor is relatively small.
Low | 3 years (P3 equivalent) | These issues introduce a low probability of contact risk and at the minimum do not comply with SCE’s construction standards. Remediation is recommended for compliance to SCE’s standards.

## Slide 25: Examples of High Priority Issues

## Slide 26: Missing Dead-end Covers
The highest number of issues is the “Missing dead-end cover” category
  Exposes bare conductor at dead-ends
  Poses a contact with object risk
Additionally, inspections found that the wrong cover was used for the dead-end in the field leading to exposed bare conductor
  Some structures with the wrong dead-end cover were sufficiently covered
Per the Distribution Overhead Standard (DOH CC 150.2):
  Dead-ends shall be covered with a Dead End Clamp in covered conductor systems.
  Covering dead-ends will ensure that stripped portions of the covered conductor at the dead-end will be protected from contact
  Dead-end Clamp Cover
Missing Dead-end Cover
Insufficient Protection

## Slide 27: Missing Lightning Arrester on Equipment Pole
SCE’s covered conductor standards require lightning arresters to be installed in (DOH CC 130)
  Remote Automatic Reclosers (RARs)
  Remote Sectionalizing Reclosers (RSRs)
  Capacitors
  Line Voltage Regulators
  Potential Transformers (PTs) associated with Remote Control Switches (RCSs)
  PTs associated with Overhead Preferred Emergency (PE) Equipment
  Overhead Transformers (All installations)
  Branch Line Fusing Installations
  Underground Dips

## Slide 28: Using jumper: PGW instead of covered conductor
Instances where Protective Ground Wire (PGW) were being used as a jumpers were identified during inspection
Using PGW as jumpers on a 1/0 covered conductor system will create a fuse
  #4 PGW ampacity is 157 A
  1/0 ACSR Covered Conductor ampacity is 271 A
Per SCE’s standard, PGW shall be used over taps when applicable and on high side bushing on transformer banks and capacitor banks (DOH DC 535)
  The use of PGW in this application is incorrect as it will not be able to meet the ampacity for 1/0 ACSR covered conductor

## Slide 29: Excessive Angle
SCE’s design and construction standards provide limiting angles on crossarms (DOH DC 575)
Structure shown in image has an angle of 40º with 1/0 Covered Conductor
  Per the standards, structure should be built with at least a double crossarm

## Slide 30: Over-tensioned Conductor
1/0 CC ACSR failed at the dead-end shoe.
Possible failure mechanism could be due to combination of:
  Presence of Ice
  Over-tensioning of Line
Analysis found that the actual constructed tension was approximately 55% greater than the maximum design tension
  Actual constructed tension 2,184 lbs
  Maximum design tension: 1,415 lbs

## Slide 31: Reference Slides

## Slide 32: Notes on 6/15/2020 Discussion
Status on follow-up actions:
  Reinforce SCE standards on wildfire mitigation by issuing Operating Bulletins, presenting to wildfire information summit, and holding re-training sessions
    Operating bulletins:
      completed two bulletins for reinforcement on proper tension and using appropriate stripping tools
      In progress: lightning arrestors and deviation angle. Reinforce DSN with planning
    Wildfire information summit:
      No longer exists
      Repurpose to quarterly standards information summit, planned for early August
    Re-training sessions
      Cannot hold in-person training since due covid-19
      Substitute with virtual training or self training, design for SCE and contractor construction – Hunly/A. (Ted Peters to help facilitating the contractor training)
        Hold a strategy session with Pam and Ted on how to properly disseminate training materials or training to contractor
  Issue “go-back” fixes to correct construction and bring up to SCE standards
    Checked in with QC inspection (Tim Garcia) – will communicate to inspector on issues Engineering identified/schedule quarterly meeting with Tim
    Worked with regional managers for correcting over-tensioning – rectifying by regions (San Jaoquin, North Coast)
    Met with Bola/Terry/Tracy. Delivered the detail FLOCs list. Terry asked us to id types of issues: supply chain, standards issues, planning and construction. Need to close the loop with Terry.
  Incorporate findings into inspection programs (ODI, OCI) to reinforce standards
    Met with Ray on ODI, Cindy, Tobie – provided engineering checklist to ODI. Ask Hunly to validate this check list with Ray to make sure six items identified on the ODI
    CC accounting field survey. Brought OSMOSE, considering adding to
  Reformat the Distribution Design Standards to create a dedicated wildfire mitigation section
    Projected on Q3 publication – Araya/Alaira leading with other input.
  Recommend that all covered conductor installed to date be inspected for compliance to Design and Construction Standard (approximately 450 miles remaining) – cost impact $2.75 M (contractors), or 5 full time inspectors + $250k (SCE resources)
    Our goal was to have HDR to complete the remained 450 miles – this is a most likely overhead and was seeking stage gate funding. However, this is delayed for alignment
    While preparing for this, Bob Scholler approached and explored opportunity to include in CC field survey scope (Osmose company was selected.) I provided Bob with the checklist but at a SLT meeting Greg/Paul agreed to move forward without CC standards inspection because field survey was more pressing and needed to get it done.
    The FLOC list with found issued was sent to Terry/Bola for field mitigation
    Discussion with regions to mitigate over-tensioning spans, especially on high-elevation (ice build-up)
  We need to think about:
    Who’s more effectively conduct inspection on 2018, 2019 installed CC (i.e. expired warranty). What are options for inspections? Meaning who can do this?
    Evaluate risk-informed criteria of found issues – seems like only PGW has greater risk, but not for end-of-line radials with small load/ampacity
    How to improve construction quality inspection for both SCE and contractors on 2020 and 2021 installation? Is there another group of inspectors, who inspect construction contractor work? If there’s, this is the group we can influence.
    How to issue correction notifications along with inspection?
    What is the scope of stage-gating approval? Is it just for funding or overall issues?
DRAFT

## Slide 33: Inspection Results Timeline
Inspection period ranges from 8/21/2019 to 3/2/2019
Note that data does not include inspections after 3/2/2020 due to delay from IKE in providing the data. This delay is due to limitations as a result of Covid-19.
Chart: Summary of Cummulative Results Timeline
| 43709 | 43739 | 43770 | 43800 | 43831 | 43862 | 43891 | 43922
% Issues Found | 0 | 0.061069 | 0.33555 | 0.37222 | 0.34473 | 0.375 | 0.29838 | 0.29562
% No Issues Found | 1 | 0.93893 | 0.66445 | 0.62778 | 0.65527 | 0.625 | 0.70162 | 0.70438
Chart: Timeline of Total Structures Inspected
| 43709 | 43739 | 43770 | 43800 | 43831 | 43862 | 43891 | 43922
Total | 44 | 131 | 301 | 540 | 731 | 968 | 1354 | 1370

## Slide 34: Covered Conductor Inspection Process

## Slide 35: Inspection Summary
Engineering contractor inspected approximately 50 circuit miles of covered conductor installation since September of 2019
Inspection data are from the following circuits
  Chawa, Galahad, Maguire, Mulholland, and Davenport
Inspections show that approximately 1/3 of line constructed will need to be remediated
The highest observed issues were missing wildlife covers, which is considered a high priority
Engineering made recommendation on priority of remediation based on potential failure risk
Summary of gaps to be addressed were also provided

## Slide 36: Comparison to Aerial Overhead Inspections (AOI)
One of the main focuses of the Covered Conductor Inspections is checking the adherence of existing construction to the Distribution Overhead standards
Proactively assessing construction gives SCE the opportunity to mitigate any issues before further escalation
In comparison, the Aerial Inspections focus solely on remediating any existing issues which may pose an active wildfire threat. The purpose is not to assess the adherence of the existing construction to the standards.

## Slide 37: Breakdown of Results
Note: A structure may have more than one issue
Issues | Number of Structures | % of Structures
Missing Wildlife Covers | 314 | 22.9%
Missing Dead-end Covers | 222 | 16.2%
Missing Fuse Covers | 99 | 7.2%
Missing Connector Covers | 61 | 4.5%
Missing Switch Cover | 5 | 0.4%
Missing Lightning Arrester Cover | 1 | 0.1%
Missing Equipment Bushing Cover | 1 | 0.1%
Missing Pothead Cover | 1 | 0.1%
Structures missing Lightning Arrester on Equipment Pole | 92 | 6.7%
Excessive Angle | 51 | 3.7%
Over-tensioned | 12 | 0.9%
Partially exposed conductor | 27 | 2.0%
PGW Jumper | 5 | 0.4%
Wrong Insulator | 1 | 0.1%

## Slide 38: Over-tensioning
Over-tensioning the lines will mechanically stress the conductor and could lead to premature failure
In order to confirm the over-tensioning, the lines in question were surveyed using a Nikon Total Station.
  Spans adjacent to the failed spans were also analyzed
The Total Station provides the following data points from which the catenary can be modeled and the tensions calculated:
  Incline between structures
  Span Length
  Sag at the midspan

## Slide 39: Tension Analysis Results - Tanager
The maximum design tension1 for 1/0 Covered Conductor is 1415 lbs
The rated breaking strength of 1/0 Covered Conductor is 4160 lbs
Results:
  The actual design tensions of all surveyed spans exceed the maximum design tension of 1415 lbs
  The tension with the presence of 1.5 inches of ice or greater with no wind for all surveyed spans will exceed the conductor’s breaking strength
  For Bare 1/0 ACSR using the same constructed sag (span 734808E to 734809E)
    Actual Constructed Tension1: 1659 lbs (over-tensioned)
    Tension for 2” ice, 0°F and no wind: 5780 lbs
Tanager | Tension (lbs) |  |  | 
Span | Actual Constructed Tension1 | 1" ice, 0°F, No wind | 1.5" ice, 0°F, No wind | 2" ice, 0°F, No wind
734808E to 734809E2 | 2184 | 3150 | 4631 | 6265
724809E to 734810E | 2138 | 3105 | 4588 | 6222
724810E to 734811E | 1932 | 2918 | 4431 | 6100
Tension for Heavy Loading Criteria: 0.5” ice, 0°F, 6 lbs wind
Failure occurred at this span. This span was reconductored after the failure, therefore the values provided may not reflect the tensions on the day of the failure

## Slide 40: Tension Analysis Results - Mettler
The maximum design tension1 for 1/0 Covered Conductor is 1415 lbs
The breaking strength of 1/0 Covered Conductor is 4160 lbs
Results:
  The actual design tensions of all surveyed spans do not exceed the maximum design tension
  The tension with the presence of 2 inches of ice or greater with no wind for all surveyed spans will exceed the conductor’s breaking strength
  For Bare 1/0 ACSR using the same constructed sag (span 4779432E to 20774T)
    Actual Constructed Tension1: 1022 lbs
    Tension for 2” ice, 0°F and no wind: 4272 lbs
Mettler | Tension (lbs) |  |  | 
Span | Actual Constructed Tension1 | 1" ice, 0°F, No wind | 1.5" ice, 0°F, No wind | 2" ice, 0°F, No wind
20774T to 4902721E | 1194 | 1925 | 3081 | 4375
4779432E to 20774T2 | 1363 | 2124 | 3305 | 4611
Tension for Heavy Loading Criteria: 0.5” ice, 0°F, 6 lb wind
Failure occurred at this span. This span was reconductored after the failure, therefore the values provided may not reflect the tensions on the day of the failure

## Slide 41: Wire Down Failure Analysis
Engineering performed additional failure analysis on the ice-loading wire down incident
The conductor from the Mettler wire down was analyzed by the root cause analysis team
Analysis found:
  Aluminum strands have been nicked during stripping process
  One strands shows to have been nicked through 50% of its cross section
    This reduces the total breaking strength by approximately 4%
    Multiple nicks in other strands will add up
Nicking of the conductor will cause the conductor breaking strength to decrease
Nick damage

## Slide 42
Covered Conductor Self-Directed Training

## Slide 43: Remediation Plans
List of Issues​ | Remediation
Missing Wildlife Covers​ | See below
Missing Dead-end Covers​ | Install Dead-end covers
Missing Fuse Covers​ | Install Fuse Covers
Missing Connector Covers​ | Install Connector Covers
Missing Switch Cover​ | Install Dead-end covers and install covered conductor jumpers (approximately 30 ft for 3 phases)
Missing Lightning Arrester Cover​ | Install Lightning Arrester Cover​
Missing Equipment Bushing Cover​ | Install Equipment Bushing Cover​
Missing Pothead Cover​ | Install Pothead Cover​
Structures missing Lightning Arrester on Equipment Pole​ | Install Lighting Arrester
Excessive Line Angle​ | Add crossarm to pole and install dead-ends or pole top insulators
Over-tensioned​ span | Re-string new covered conductor
Partially exposed conductor​ | Install connector covers or split tube to cover exposed sections
PGW used as a jumper on the primary (does not have enough ampacity) | Replace PGW jumper with covered conductor jumper (approximately 30 ft for 3 phases)
Wrong Insulator Installed​ | Replace existing insulator with Vice Top Insulator
Aeolian Vibration | Install vibration dampers

## Slide 44
Chart: Summary of Results
| Wrong Insulator | Missing Lightning Arrester Cover | Missing Equipment Bushing Cover | Missing Pothead Cover | PGW Jumper | Over-tensioned | Partially exposed conductor | Excessive Angle | Missing Connector Covers | Missing Lightning Arrester on Equipment Pole | Missing Fuse Covers | Missing Dead-end Covers
High | 1 | 1 | 1 | 1 | 5 | 12 | 25 | 51 | 64 | 92 | 99 | 218
Critical
High
Medium
Low