## Slide 1: Grid Resiliency Program Management Office Discussion Topics: - Veg Management QC - Reliability Operation Center (ROC) Wildfire Mitigation Activities - Non-WMP Wildfire Risk Reduction Activities (Part 1 - LSI & Hardware)
Wildfire Governance Forum – July 17, 2020

## Slide 2: Topic #1 – Veg Management QC Program

## Slide 3: Defense in Depth Oversight Strategy
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292
Vegetation Management (VM) uses this strategy to provide reasonable assurance that vegetation encroachments into SCE’s facilities are minimized. It includes the following:
Post Work Verification – Performed by VM Senior Specialists who are certified arborists. SSPs sample approximately 5% of work performed in their jurisdiction on a monthly basis and provide feedback/document need for rework
Independent Quality Control (QC) Inspections – Performed by contractors who are certified arborists. A high rate of sampling is performed to verify pre-inspectors and pruners are performing to expected standards. 100% inspection is performed on highest risk circuits*
Quality Assurance (QA) reviews – Performed by internal QA personnel to verify program compliance to internal standards and external regulations. Results of assessments drive programmatic continuous improvement.
Additional Defenses:
Supplemental Patrols – During summer months, VM contractors and Senior Specialists revisit areas to provide added assurance that SCE facilities are free of vegetation encroachments prior to fall weather. These include Operation Santa Ana, Canyon Patrols and Summer Readiness Verification Patrols.
Internal Audits – Regular operational audits performed by ASD include field reviews
*Note: QC is performed on 100% of the top ~94% REAX risk circuit miles. QC confidence level (CL) / confidence interval (CI) for the remaining circuit miles in HFRA is 99/1.7% and Non-HFRA exceeds 95/5%.

## Slide 4: Program Parameters - Line Clearing
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292
Focus is tracking contractor performance against required standards
Acceptable Quality Levels (AQL):
  100% AQL for Regulatory Clearance Distance (RCD) – compliance clearance
    E.g., 4’ for Distribution in HFRA
  95-98% AQL for the Compliance Clearance Distance (CCD) – internal standard
    E.g., 6’ for Distribution in HFRA (1.5 x RCD)
Other aspects measured include:
  Grid Resiliency Clearance Distance (GRCD) which is expanded clearance – CPUC recommendation, not enforceable
    E.g., 12’ for Distribution in HFRA
  Contractor-specific performance, including trees missed during pre-inspection
  Pruning industry standards
  Starting July 2020, overall program health as measured by RCD and CCD distances farther into the annual cycle

## Slide 5: Implementation Timeline
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292
Q2 2019
April – Line clearing QC commenced
  Focus on contractor performance; within 60 days of work completion
June – Hazard tree QC of mitigations commenced (100%)
Q1 2020
AQLs established for RCD and CCD
New contracts in place with 5 prime pruning and 4 pre-inspection contractors
Q2 2020
HTMP QC of assessments commenced
Q3 2020
Line clearing – commenced inspections for work completed >60 days
Vendor Corrective Action Program under development; implementation in 1Q 2021
Q4 2020
AQL to be implemented for Grid Resiliency Clearance Distance (GRCD)
Dead/Dying tree program QC will commence

## Slide 6: 2020 YTD Performance (through June)
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292
Trends/Issues:
Overall 2020 performance has improved from 97-98% in 2019 to >99% in 2020
Recent results (May-June 2020) show a decline in performance, reducing YTD conformance rate
Distribution – Uncertainty in drivers for minor decline in performance
  Consistent across most contractors
  Seasonal growth and increased conductor loading may be a contributing factor; however, clearance is required to factor in growth of species to last for an annual cycle
Transmission – Related to pre-inspection issues with two contractors incorrectly using LiDAR to determine clearance under maximum line dynamic conditions
  Current field conditions may not approach maximum sag/sway
  39 circuits and approximately 933 circuit miles impacted
  ACTIONS TAKEN – Discussions and training for contractor personnel on usage of LiDAR; developing plan for re-inspection for all circuits inspected by the two contractors
Distance | Target/AQL | Overall Result | Distribution | Transmission
RCD | 100% | 99.11% | 99.20% | 96.78%
CCD | 95%-98% | 95.25% | 94.56% | 93.38%

## Slide 7: 2020 YTD Performance – RCD Overall
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292

## Slide 8: 2020 YTD Performance – RCD HFRA
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292

## Slide 9: Corrective Action Approach
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292
Regular Feedback
Monthly, QC results are trended, incorporated into scorecards, and detailed feedback on performance is provided to pre-inspection and pruning crews
When needed, Corrective Actions are issued to address performance shortfalls
  May involve additional measures such as heightened QC inspections by each contractor, additional training of field personnel, and onboarding of additional resources
Performance Issues
QC data segregates performance by location and contractor to drive understanding of gaps
One contractor is significantly underperforming their peers for both pre-inspection and pruning
  VM QC is routinely meeting with contractor to address performance shortfalls
  If improvement is not observed, additional Corrective Actions will be issued
  Work is largely in non-HFRA

## Slide 10: Appendix - Veg Management QC Program

## Slide 11: 2020 YTD Performance – GRCD Overall

## Slide 12: 2020 YTD Performance – GRCD HFRA

## Slide 13: Line Clearing Sampling and Other Detail
overall_0_132083107041691217 columns_2_132048702459405524 7_1_132048702466692635 10_1_132048702466852189 21_1_132048721872633283 23_1_132049640018006217 26_1_132049645698177263 29_1_132083107019594412 33_1_132083107019594412 13_1_132083204190616292
Sampling Targets
Vegetation QC is performed on a “circuit mile” basis
  8,145 total miles inspected (HFRA and Non-HFRA)
  6,125 total HFRA miles inspected
Leverages REAX risk model to inform sampling
  Includes 100% of the highest risk HFRA circuit mileage – 2,161 miles representing 93.87% of risk
  Lower risk HFRA circuit miles are sampled using a CL/CI of 99/1.7%
  Non-HFRA circuit mileage sampling exceeds a CL/CI of 99/5%
YTD Status:
  At 42% of 8,145-mile target
  At 85% of achieving 2020 WMP goal of 3,000 HFRA circuit miles
Staffing
QC is managed by internal SCE VM staff (Senior Manager and 2 x QC advisors)
QC is performed by contractor California Forestry Vegetation Management (CFVM)
  26 personnel dedicated to line clearing QC (of 32 total; targeting increase to 40)
Distances

## Slide 14: IOU QC Comparison

## Slide 15: Topic #2 - Reliability Operation Center (ROC) Wildfire Mitigation Activities

## Slide 16: Reliability Operations Center Overview
The ROC was developed to use advance analytics and machine learning to find solutions for increased safety and enhanced reliability
  The team has increased the use of the smart meter capabilities and big data to leverage the 5 million points on our grid that provide insight and answers both in near real-time and through big data analysis
  The organization has developed a team of Data Scientists, Power System Operators and Technical Sr. Specialist who work together to find solutions that can be applied to our operations
This focus has incorporated many efforts to reduce ignition risk since early in its inception with the following key focus areas
  Distribution Fault Anticipation (DFA) & Distribution Fault Recorder (DFR)
  Asset Defect Detection
  Meter Alarming of Downed Energized Conductors (MADEC)
  Identify Energy Theft & Hazardous Condition
  PSPS Support

## Slide 17: Distribution Fault Anticipation (DFA) and Distribution Fault Recorder (DFR)
The ROC provides analytical support to the project teams (under T&D Apparatus & Linear Strategies) to evaluate events detected by either DFA or DFR devices
  The DFA is a product in collaboration with Texas A&M installed at the substation circuit level to collect data and produce an alarm on potential problems in the system
  The DFR is a standard product installed at the substation circuit level which records granular waveforms that can be used to create unique algorithms.
The ROC began work on the DFR effort in Q3 2019 and the DFA effort in Q4 2019
  Both pilots are ongoing by the project teams while the evaluations continue to inform decisions for the future
  Success criteria for these pilots are being refined to facilitate future go/no-go decision points
Over eighty events have been evaluated by the ROC since the inception of the DFA pilot. This information is leveraged info for GRC rebuttal responses
The ROC continues to look for solutions to the two main challenges for this technology
  The ability to identify actionable events from normal grid activity
  The ability to locate the event on the circuit when and actionable event is triggered

## Slide 18: Distribution Fault Anticipation – Events Analyzed YTD

## Slide 19: Asset Defect Detection
Use machine learning artificial intelligence model to identify damage/defects in the aerial inspections images to provide a priority list of images to the inspectors
  Find defects quicker with priority inspection
  Provide an additional process to ensure no defect is missed
  Continue to improve the model through feedback from the inspectors
The ROC has been developing our model since mid 2019 and is currently working with IT and the Aerial Inspection team to incorporate into their process through a pilot
The model is currently tuned to identify crossarm defects and can scan up to ~10,000 images in a day based on current computing power. More computing power will enable greater quantities to be processed prior to inspector review
Initial pilot is scheduled to launch in July. The addition of poles, transformers and insulators to the model will begin once we get regular feedback from the pilot

## Slide 20: Asset Defect Detection
The red triangles in the thumbnail images tell the inspector the model has detected a defect.
The pop-up box (which can be moved, closed and reopened) allows the inspector to provide essential feedback to the model so it can learn and improve

## Slide 21: MADEC Overview & Automation with EMS
Meter Alarm Down Energized Conductor detects an energized wire when essential smart meter data is delivered from the field
By improving the automation of the alarm to the switching centers we improve the operational process to ensure action and reduce time
MADEC has been operational since January 2019; additional automation to deliver the alert directly into the Energy Management System (EMS) went into production on June 22, 2020
There has been a 3x improvement in the speed of response time from alarm to de-energization since the implementation in EMS
  Pre EMS implementation: 2020 average = 7.2 minutes
  Since EMS integration June 22, 2020 average = 2.4 minutes
The ROC is also working with Meter Engineering and IT-Advanced Metering Operations to enable smart meter voltage alerts on commercial poly phase meters and other additional enhancements
  Expand MADEC to detect wire down conditions where commercial poly phase meters are present
  Evaluate if the algorithm can be updated to detect Covered Conductor

## Slide 22: MADEC Overview & Automation with EMS
*Red box shows wire on ground

## Slide 23: Identify Energy Theft & Hazardous Conditions
Use smart meter voltage, tamper and other data to identify potential energy theft or other hazardous conditions.
Initiated work with the Revenue Protection team in late 2018. Developed initial machine learning algorithm solution in mid 2019 which continues to learn and improve
The process has identified 125 hazardous energy theft and other conditions reducing the risk of ignition at these locations
The process is currently limited by the capacity of the field investigators to receive more identified accounts (predictions).
The algorithm identifies hundreds of accounts each month but only 20-25 are sent to the field due to manpower capacity
*Significant cable degradation. Loss of insulation in handhole.

## Slide 24: Identify Energy Theft & Hazardous Conditions

## Slide 25: PSPS Support
Integrate a ROC Data Scientist in the PSPS ACE team
Supporting PSPS automation and improvement efforts through developing automation scripts and data analysis while utilizing ROC teammates for solution support
The ROC will continue to provide direct and indirect PSPS support through our embedded resource and through ROC team engagement on multiple levels
  Sr. Specialist Team – Continue to provide PSPS IMT Support
  Power System Operators – Continue to provide field analysis support for PSPS efforts
  Data Scientists – Work with our dedicated ACE team resource to deliver solutions while working to develop new tools and processes for better real-time situational awareness

## Slide 26: Topic #3 – Non-WMP Wildfire Risk Reduction Activities Part 1 - Long Span Initiative (LSI) & Hardware

## Slide 27: Executive Summary
Long Span Initiative (LSI)
LSI consists of 5 category of spans (long/mixed, angle, slack, transition, 300-350’ ACSR)
~9.3k structures identified inception to date for remediation
Key Accomplishments
Remediated the highest risk (top 2%) of Long Spans with 2019/2020 priority due dates
Completed aerial inspections for ~30k structures1 to date
Distribution Hardware (HW)
During 2019 inspections, steps were taken to catalog additional HW equipment that could potentially have fire risk but not driven by GO95 compliance:
  Track opportunities to repair known issues with planned work (with existing P1’s/P2’s or via other programs such as Covered Conductor)
  Evaluate HW equipment fire risks to determine if any remediations should be done proactively
Key Accomplishments
Created ~96k “E8”3 notifications (not GO 95 compliance driven)
These hardware risks are low, however, risk analysis prioritized 200 structures2 to be proactively remediated based on wildfire risk
These structures are in the process of being added to distribution remediation scope
One structure can have multiple spans.
One structure can have multiple hardware notifications.
E8 is a new notification classification to track non elevated fire-risks.

## Slide 28: Long Span Initiative (LSI) Summary
 | LSI Category (structures) |  |  |  | 
 | Long Spans & Mixed Conductor | Angle Spans | Slack Span | Transition Spans | 300’ – 350’ ACSR
Population | ~38k | ~174k | ~17k | ~10k | N/A
Inspection1 | ~38k | ~5k | ~17k | ~9k | ~13k
Notifications | ~9k | TBD | TBD | TBD | TBD
Completed | ~4k | TBD | TBD | TBD | TBD
Remaining | ~5k | TBD | TBD | TBD | TBD
400k spans identified in SCE’s original HFRA; remaining scope will be adjusted to account for new HFRA boundary
LSI categories below were inspected during ground EOI inspections and remaining are being inspected through Aerial LiDAR
Conductor type and span length was used to determine which population needed to be inspected for each category
Spans identified with notifications will be risk-prioritized for remediation
Long Span & Mixed Conductor is the only category with remediations completed thus far
Note: TBD items are being inspected.
1 Classifications can include duplication of structures

## Slide 29: LSI Inspection Progress
Current Status
~78k unique structures are in inspection scope
  ~27k inspected by ground inspections during EOI
  ~51k originally scoped for aerial inspection LiDAR data capture
    ~44k remain due to removal of ~7k of aerial inspection scope due to HFRA boundary changes
    ~30k LiDAR data already captured
Risks & Issues
Expected finish of 2020 flights is moving from July to September
Need to add 17% of remaining LiDAR capture into vendor scope package
Chart: 
| Flights Completed (LiDAR Captured) | Flights Scheduled (Done by Sept) | Unallocated Scope (Schedule or Remove) | Not in HFRA (Removing from Scope)
 | 29626 | 6035 | 8548 | 7268
2019/2020 Capture
~51k LiDAR Capture Status

## Slide 30: LSI Remediations using LiDAR Data
Progress to Date
LiDAR data processed for ~10k of ~30k structures captured1 and developed a script to flag span issues2
  The script flags issues with conductor sag, phase spacing, insulator spacing and conductor heights of attachment
  Initial screening has flagged ~6.4k structures having issues that include reduced pin spacing, improper sag and potential conductor clashing
Structures with issues will require further review by distribution planning to identify remediations
  Planners will use a GIS desktop tool to verify field conditions and assign the remediation type (e.g., spacer, larger cross arm, ridge pin/box construction, or re-conductor/covered conductor)
Key Next Steps
Review the LSI scope, secure distribution planning resources, and set schedule (July-August)
Identify and risk prioritize remediations (August-Q1 2021)
Notes:
Takes ~4-8 weeks to receive processed LiDAR data from vendors once flights are completed. Vendor is behind schedule and more time has been needed for go-backs. Working with the Aerial Inspection team to improve schedule for delivery of processed LiDAR data and identify opportunities to accelerate.

## Slide 31: LSI Aerial Inspection & Remediation Timeline
Task | Timing | Q1 2020 | Q2 2020 | Q3 2020 |  |  | Q4 2020 |  |  | Q1 2021 |  |  | Q2 2021
 |  | Jan-Mar | Apr-Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr -Jun
Flights Scheduled |  |  |  |  |  |  |  |  |  |  |  |  | 
Process LiDAR Data |  |  |  |  |  |  |  |  |  |  |  |  | 
Flag Span Issues & Assign Remediations |  |  |  |  |  |  |  |  |  |  |  |  | 
Risk Analysis, Approval of Mitigations, Finalize Execution Plan |  |  |  |  |  |  |  |  |  |  |  |  | 
2020 Plan
Remaining Scope
2020 Capture
Remaining Scope
2019 Capture
Delays to the original inspection schedule has impacted timeline
  Weather, vendor performance, scope changes, data validation
Team evaluating options to improve schedule
  Phased approach (pre-approval) and prioritizing high REAX areas
Other factors that may impact include finalizing schedule for remaining scope and vendor processing time

## Slide 32: Distribution Hardware (HW) Status
~96k “E8” notifications1 (not GO 95 compliance driven2) were generated for tracking distribution HW equipment fixes
  P2’s already created for compliance issues identified during 2019 inspections
~18k of the 96k notifications are associated with existing P2s2 and will be addressed at that time; remaining are being tracked for future opportunities
~9k lightning arrestors notifications will be added (by the end of July) for a total of 105k notifications
341 HW issues (on 200 structures) were risk-informed to be remediated proactively
Hardware Type | E8 P2/P3 Count
Automatic Splices | 1,913
Fuse Link | 7,432
Guy Wire - Automatic | 42,318
Guy Wire - Both | 9,299
Liquid Fuse | 3,613
No Bird Guard | 25,901
No Bird Guard/Pothead | 1,739
Open-Wire (Bare) Conductor | 2,623
Preform Splices | 1,185
Total Batched to Date | 96,023
Lightning Arrestors (in-process) | 9,034
Total Population | 105,057
Notes:
1. E8s are minor system hardening notifications. 2. To date, ~17,6k HW E8 P2’s/P3’s are located on poles with existing P2 notifications and planned to be addressed at the same time to meet the “clean the pole” tenant. Counts will fluctuate as notifications are completed and new notifications are generated.

## Slide 33: Appendix - Long Span Initiative & Hardware

## Slide 34: LSI Remediation Status
Long Span & Mixed Conductor | P2 Counts
Completed to Date | 3,895
Pending Highest Risk (Top 2%)2 | 73
Pending (Outside Top 2%) | 5,305
Deleted | (104)
Total Existing P2 Notifications | 9,311
Notifications | 20204 | 2021 | 2022
Top 2% (w/in 6-12 mos.) | 7 | 0 | 0
Remaining HFRA (up to 3 yrs.) | 8 | 0 | 4,394
Non-High Fire (up to 3 yrs.) | 0 | 4 | 899
Remediation Execution Summary
Pending Remediations by Due Date
Notes:
1. Concurrence for risk-based prioritization and notification due dates with ERM and Legal
2. Top 2% of LSI P2’s were scoped in accordance to HFRA notification timelines (e.g., 6 months for Tier 3 and 1 year for Tier 2)
3. Q2 WMP goal for remediations met; 7 in the top 2% pending due to GO95 exceptions (permit or access issues)
4. Includes 5 notices from 2019 (carried over) due to GO95 exceptions
Current Status
3,895 LSI P2’s have been completed to date
The highest risk (top 2%) of LSI P2’s have been remediated
  This represented 50% of the total risk
Remaining P2’s are classified as non-elevated fire1 and given a max of 3 years to complete (from the inspection date), and are bundled/prioritized with other work