## WMP Data Request
DATA REQUEST SET | QUESTION NUMBER | QUESTION | RESPONSE | DATE RECEIVED | DATE COMPLETED
MGRA-SCE-001 WMP 2021 | 001 | Please provide the most recent available geodatabase comprised of the non-confidential portion of the GIS data uploaded to the WSD website. This should contain the least the version of GIS data provided to WSD in September pursuant to the Draft WSD GIS Data Reporting Requirements and Schema for California Electric Corporations (Draft GIS Data Schema) along with any updates provided in December. Where confidential data is intermixed in tables with non-confidential data, fields containing confidential data should be left blank or removed. Confidentiality should not be applied at the feature class level. | As explained in its Quarterly Reports, SCE has reservations regarding confidentiality of data. Data is confidential when it is in the public interest that the information not be disseminated publicly. Release of the precise location, age, and other attributes of SCE’s assets alongside the precise location of critical facilities may significantly increase safety risk to the public. For example, knowledge of underground line routes and electrical equipment serving a critical facility could facilitate an attack on that critical facility’s power supply. Also, knowledge of the location of specific SCE assets in areas with historical high fire weather could make them vulnerable to attack during the worst possible time. Further, the precise locations of SCE’s high voltage transmission lines and substations alongside the abovementioned confidential information, as well as the non-confidential information requested increases risk to the bulk power transmission system. The Commission recognizes the importance of safeguarding critical energy infrastructure information and although maps of varying age and detail of SCE’s transmission system may be publicly available from other sources, SCE does not believe it is prudent to further propagate that information, in this level of detail, accompanying other information that, taken together, could prove to be useful to a bad actor. According to CAL FIRE, arson arrests through September/October 2020 are approximately 60% greater than the annual average over 2016 through 2019. This is concerning to SCE and should be a concern to stakeholders and the Commission. For these reasons, SCE applied confidentiality at the feature class level for each provided dataset as opposed to the data field level. Notwithstanding these concerns, SCE is working towards identifying confidentiality at the field level for its next Quarterly Report submission. Given the constraints of the draft GIS Data Schema, it may not be possible to replicate the Geodatabase with just non-confidential data. Moreover, while a data element such as equipment age may be deemed non-confidential on a standalone basis, when that data is related to location and probability and consequence of ignition information, it could provide critical information to a bad actor putting SCE facilities and communities at grave risk. As such, even non-confidential data elements in a relational Geodatabase could pose a significant risk. Standard Commission confidential processes require stakeholders to enter into Non-disclosure Agreements (NDAs) to protect confidential information and SCE recommends these processes be used with stakeholders requesting the Geodatabase until the WSD creates its data portal with strict security protocols. To meet this request, SCE is providing four data layers that it determined are non-confidential. Also, SCE plans to identify confidentiality at the data element level with its next Quarterly Report submission and will assess if it is possible and in the public interest to recreate a non-confidential Geodatabase that could be provided. The four non-confidential data layers (Camera, Weather Station, OH Primary Distribution Line, and OH Secondary Distribution Line) are attached. | 2021-01-07 | 2021-01-12
MGRA-SCE-001 WMP 2021 | 002 | If updates to the GIS database are to be released to WSD contemporaneously with the Wildfire Mitigation Plans, the IOUs shall make non-confidential versions of the GIS data available to MGRA and other interested stakeholders at the same time that they are released to WSD. Deadline for this request is therefore the same as that for GIS data release to WSD. | Please see SCE’s Response to Question No. 1. | 2021-01-07 | 2021-01-12
MGRA-SCE-002 WMP 2021 | 001 | Please provide the most recent available geodatabase comprised of the non-confidential portion of the GIS data uploaded to the WSD website containing PSPS Event records including specifically all perimeter, timing, and damage data that is reported to WSD and to the Safety Enforcement Division as part of PSPS event reporting. Damage records should include at the least location, type of damage, any photos, and date and time of report. Customer meter records may be omitted from the data response. | Please see the attached geodatabase. | 2021-01-25 | 2021-02-10
MGRA-SCE-002 WMP 2021 | 002 | Please provide the most recent available geodatabase comprised of the non-confidential portion of the GIS data uploaded to the WSD website containing ignition data that is reported to WSD as part of risk event reporting. Please provide entire the historical data set available within the database. | Please see the attached geodatabase. | 2021-01-25 | 2021-02-10
MGRA-SCE-002 WMP 2021 | 003 | Please provide the most recent available geodatabase comprised of the non-confidential portion of the GIS data uploaded to the WSD website containing outage data that is reported to WSD as part of risk event reporting. Please provide entire the historical data set available within the database. | Please see the attached geodatabase. | 2021-01-25 | 2021-02-10
MGRA-SCE-002 WMP 2021 | 004 | To the extent that there are any records or fields considered confidential in the above datasets, please provide a list of the type of record (for example, transmission with voltage above 200 kV) and specific fields that are considered confidential, including explanation and legal justification for why the particular type of record or field is considered confidential. | Pursuant to the WSD’s Draft GIS Schema requirements, SCE identified confidentiality at the data field level in its GIS Status Report. As such, the list of fields considered confidential are included in SCE’s GIS Status Report. SCE’s GIS Status Report can be found on its WMP webpage (www.sce.com\wmp). Pursuant to CPUC rules, SCE submitted a confidentiality declaration to the WSD regarding data it deems confidential. That declaration explains the confidentiality basis as follows: The information meets the balancing test of California Government Code section 6255. It is in the public interest that the information not be disseminated publicly. Release of detailed asset and risk event information could make SCE’s facilities vulnerable to attack and could be valuable information in planning an attack on critical infrastructure. Further, providing this information in addition to and in relation with Critical Facility information could further the consequences of such an attack. There is little to no benefit to making this information publicly available. Third parties do not need this information to evaluate SCE’s 2021 WMP Update. As such, the public interest in not disclosing this information far outweighs the public interest in disclosing it. In addition, public disclosure of customer information could compromise privacy to the potential harm of customers. In addition, public disclosure of this information could identify the company, customer, or the location/site or other private information that could be advantageous to a competitor. Gov’t Code § 6254(c); Gov’t Code § 6254(k); Civil Code §§ 1798.3 & 1798.24 (the California Information Practices Act); Cal. Const., Art. I, § 1 (California constitutional right to privacy); Gov’t Code §§6254(k), 6254.7(d); Evid. Code §1060; Civil Code §3426 et seq.; Competitive Data: Gov’t Code §§ 6254(k), 6254.7(d); Evid. Code §1060; Civil Code §3426 et seq. | 2021-01-25 | 2021-02-10
CalAdvocates-SCE-2021WMP-01 | 001 | Please provide a list of all publicly owned electric utilities and electrical cooperatives (collectively, POUs) that you supply in part or whole. | Please see the attached Excel file. | 2021-01-15 | 2021-02-11
CalAdvocates-SCE-2021WMP-01 | 002 | For each publicly owned electric utility and electrical cooperative (collectively, POUs) to which you supply power, please respond to the following: a) Have you coordinated with the POU to ensure resilience of the POU during a public safety power shutoff (PSPS) event that you initiate? Please describe the nature of this coordination if so. b) In 2020, what coordination, planning, or other activities took place between you and the POU to mitigate the effect of a potential SCE-initiated PSPS event on the POU and its customers? | Yes. In 2019, SCE met with the POUs which could be impacted by an SCE event on our transmission and sub-transmission system. In these meetings, SCE reviewed the potential impact on the POUs if the circuits serving them were de-energized. SCE and the POUs also reviewed communication protocols in the event a line serving them was being monitored for PSPS or was de-energized. SCE also reviewed its WMP with the POUs. b) In 2020, SCE invited all POUs which could be impacted by PSPS to participate in SCE’s PSPS Working Groups and named the Southern California Public Power Authority to the PSPS Advisory Panel. | 2021-01-15 | 2021-02-11
CalAdvocates-SCE-2021WMP-01 | 003 | Regarding your wildfire risk model1: a) Have you developed a risk-estimation model that quantifies the wildfire risk level of each of your circuits? b) If the answer to question 3(a) is yes, explain the finest level physical granularity (i.e. individual equipment, pole/tower, circuit-segment, circuit) with which you assess the wildfire risk level of your facilities. c) If the answer to question 3(a) is yes, explain the finest level of temporal granularity (i.e. day, week, month, year) with which you assess the wildfire risk level of your facilities. d) How are transmission and distribution circuits treated differently in the model referred to in question 3(a)? e) Does the model in question 3(a) allow you to rank circuits or circuit-segments by risk level? f) Does the model in question 3(a) rank transmission and distribution circuits together or separately? g) Are your wildfire risk model’s outputs for transmission and distribution circuits comparable to each other? | a. Yes. A risk-estimation model that quantifies the wildfire risk level has been developed at circuit level in HFRA. b. SCE has developed risk models at equipment and circuit segment level for distribution circuits. The transmission models were developed at pole/tower level. c. The wildfire risk level is assessed at yearly temporal granularity. d. The transmission and distribution circuit probabilities have different data associated with them and are calculated using different models. As a result, they have different probabilities of ignition. The main difference between distribution and transmission model is the asset and available data for developing the models. e. The wildfire risk model allows SCE to rank circuits and circuit segments at risk level. f. The transmission and distribution risk scores cannot be ranked together, the two models use different data input and have different machine learning model accuracy. They both can be used to rank and make risk-informed decisions for transmission and distribution. g. The outputs for transmission and distribution circuits may be compared to each other by calibrating the scores to expected number of fires as a comparable unit. | 2021-01-15 | 2021-02-11
CalAdvocates-SCE-2021WMP-01 | 004 | Provide an Excel table of all distribution circuits existing in 2020 (as rows) that includes the following information in separate columns. Items (a) through (g) are features of the circuit. Items (h) through (ddd) pertain to work performed for each circuit. a. Circuit Name b. Total Circuit Miles c. Circuit Voltage d. Wildfire Risk Level2 e. Circuit SAIDI (System Average Interruption Duration Index) f. Circuit SAIFI (System Average Interruption Frequency Index) g. Circuit MAIFI (Momentary Average Interruption Frequency Index) h. Miles of Enhanced Vegetation Management (EVM) Work in Non-High-Fire Threat District (HFTD) Areas in 2020 i. Miles of EVM Work in HFTD Tier 2 in 2020 j. Miles of EVM Work in HFTD Tier 3 in 2020 k. Miles of Routine Vegetation Management Work in Non-High-Fire Threat District (HFTD) Areas in 2020 l. Miles of Routine Vegetation Management Work in HFTD Tier 2 in 2020 m. Miles of Routine Vegetation Management Work in HFTD Tier 3 in 2020 n. Miles of Covered Conductor Installed in Non-HFTD in 2018 o. Miles of Covered Conductor Installed in Non-HFTD in 2019 p. Miles of Covered Conductor Installed in Non-HFTD in 2020 q. Miles of Covered Conductor Installed in HFTD Tier 2 in 2018 r. Miles of Covered Conductor Installed in HFTD Tier 2 in 2019 s. Miles of Covered Conductor Installed in HFTD Tier 2 in 2020 t. Miles of Covered Conductor Installed in HFTD Tier 3 in 2018 u. Miles of Covered Conductor Installed in HFTD Tier 3 in 2019 v. Miles of Covered Conductor Installed in HFTD Tier 3 in 2020 w. Number of Poles Replaced in Non-HFTD in 2018 x. Number of Poles Replaced in Non-HFTD in 2019 y. Number of Poles Replaced in Non-HFTD in 2020 z. Number of Poles Replaced HFTD Tier 2 in 2018 aa. Number of Poles Replaced HFTD Tier 2 in 2019 bb. Number of Poles Replaced HFTD Tier 2 in 2020 cc. Number of Poles Replaced HFTD Tier 3 in 2018 dd. Number of Poles Replaced HFTD Tier 3 in 2019 ee. Number of Poles Replaced HFTD Tier 3 in 2020 ff. Miles of Underground Conductor Installation in Non-HFTD in 2018 gg. Miles of Underground Conductor Installation in Non-HFTD in 2019 hh. Miles of Underground Conductor Installation in Non-HFTD in 2020 ii. Miles of Underground Conductor Installation in HFTD Tier 2 in 2018 jj. Miles of Underground Conductor Installation in HFTD Tier 2 in 2019 kk. Miles of Underground Conductor Installation in HFTD Tier 2 in 2020 ll. Miles of Underground Conductor Installation in HFTD Tier 3 in 2018 mm. Miles of Underground Conductor Installation in HFTD Tier 3 in 2018 nn. Miles of Underground Conductor Installation in HFTD Tier 3 in 2019 oo. Miles of Underground Conductor Installation in HFTD Tier 3 in 2020 pp. Miles of Light Detection and Ranging (LiDAR) Inspection in Non-HFTD in 2020 qq. Miles of LiDAR Inspection HFTD Tier 2 in 2020 rr. Miles of LiDAR Inspection HFTD Tier 3 in 2020 ss. Number of Detailed Overhead Inspections in Non-HFTD in 2020 tt. Number of Detailed Overhead Inspections HFTD Tier 2 in 2020 uu. Number of Detailed Overhead Inspections HFTD Tier 3 in 2020 vv. Number of Sectionalization Devices Installed in Non-HFTD in 2018 ww. Number of Sectionalization Devices Installed in Non-HFTD in 2019 xx. Number of Sectionalization Devices Installed in Non-HFTD in 2020 yy. Number of Sectionalization Devices Installed HFTD Tier 2 in 2018 zz. Number of Sectionalization Devices Installed HFTD Tier 2 in 2019 aaa. Number of Sectionalization Devices Installed HFTD Tier 2 in 2020 bbb. Number of Sectionalization Devices Installed HFTD Tier 3 in 2018 ccc. Number of Sectionalization Devices Installed HFTD Tier 3 in 2019 ddd. Number of Sectionalization Devices Installed HFTD Tier 3 in 2020 | Microsoft Excel file titled “Question 4” contains the requested information. | 2021-01-15 | 2021-02-12
CalAdvocates-SCE-2021WMP-01 | 005 | Provide an Excel table of all transmission circuits (as rows) that includes the same information listed above in Question 4(a)-(ddd). | Microsoft Excel file titled “Question 5” contains the requested information. | 2021-01-15 | 2021-02-12
CalAdvocates-SCE-2021WMP-01 | 006 | For each WMP initiative listed below, please state how the Wildfire Risk Levels provided in the Excel spreadsheet for Questions 4 and 5 influenced where you performed work in 2020 and how work was sequenced. a) EVM b) Covered conductor installation c) Pole replacement d) Undergrounding e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of transmission assets i) Aerial inspections of distribution assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SCE uses a risk model that calculates risk scores at the asset level and can be aggregated to higher levels such as segment and circuit. Where possible, these activities used the output of the model to prioritize the work. a) EVM - The data provided below is for our routine compliance program, where we manage our tree inventory to the regulatory clearance. The work is performed in accordance with an annual work plan/schedule that ensures all work prescribed can be performed when factoring in things such as weather and access conditions. We do not prioritize work based on HFRA or non-HFRA status or individual risk values for our routine compliance program. b) Covered conductor installation – Covered conductor installation program used the Wildfire Risk Model (WRM) as described in the 2020 WMP to prioritize which circuit-segments were replaced with the covered conductor. However, some circuit segments that were in-flight prior to the development of the model were completed. These segments were originally prioritized by conductor size and proportion of conductor in tier 2 vs. tier 3 areas. c) Pole replacement – Poles replaced in conjunction with the installation of covered conductor followed the method described above for CC. Poles replaced through inspection programs are prioritized and sequenced to meet compliance requirements set forth in our inspection and maintenance programs. d) Undergrounding – No wildfire driven undergrounding construction was completed in 2020. e) Grid Sectionalization - As this work was targeted for completion in 2020, the work prioritization efforts were aligned with normal work execution efforts such as resource availability, permitting and rights approvals, and circuit outage coordination. Risk scores were not used to sequence or prioritize. f) Detailed inspections of distribution assets - The inspection prioritization was carried out using the WRM and grouping risk scores into a 3 by 3 grid, creating categories of risk for execution. Please refer to the 2020 WMP for details. g) Detailed inspections of transmission assets - The inspection prioritization was carried out using the fire consequence component of the WRM aggregated to the circuit level. The probability of ignition component of the WRM was not developed when transmission inspection work was scoped. h) Aerial inspections of transmission assets – Same as the method used for transmission detailed inspections. i) Aerial inspections of distribution assets – Same as the method used for distribution detailed inspections. j) LiDAR inspections of distribution assets – Risk prioritization was not performed for LiDAR inspections. k) LiDAR inspections of transmission assets - Risk prioritization was not performed for LiDAR inspections. | 2021-01-15 | 2021-02-12
CalAdvocates-SCE-2021WMP-01 | 007 | For each WMP initiative listed below, please complete Table A below, showing how much of the work you completed in 2020 was performed on distribution circuit-segments in each risk quintile. a) EVM b) Covered conductor c) Pole replacement d) Undergrounding e) Grid sectionalization f) Climbing inspections g) Aerial inspections h) LiDAR inspections | SCE has not performed an analysis nor has data readily available to provide the response requested in this format. However, the analysis can be derived from the source data found in SCE’s response to Questions 4 and 5 of this data request. | 2021-01-15 | 2021-02-12
CalAdvocates-SCE-2021WMP-01 | 008 | For each WMP initiative listed below, please complete Table B below, showing how much of the work you completed in 2020 was performed on transmission circuit-segments in each risk quintile. a) EVM b) Covered conductor c) Pole replacement d) Undergrounding e) Grid sectionalization f) Climbing inspections g) Aerial inspections h) LiDAR inspections | SCE has not performed an analysis nor has data readily available to provide the response requested in this format. However, the analysis can be derived from the source data found in SCE’s response to Questions 4 and 5 of this data request. | 2021-01-15 | 2021-02-12
CalAdvocates-SCE-2021WMP-01 | 009 | Regarding your PSPS circuit modeling capabilities: a) Please describe your present circuit modeling capabilities with regard to PSPS thresholds (“PSPS circuit modeling capabilities”), including with what level of granularity they are able to determine how circuit hardening efforts or other changes to a line segment will affect PSPS thresholds. b) Please describe any improvements to the present PSPS circuit modeling capability that you expect to enact in 2021. c) Please describe the expected state of your PSPS circuit modeling capabilities at the conclusion of the 2020-2022 WMP cycle. | a) Please generally see Chapter 8 of SCE’s 2021 WMP Update that describes our PSPS practices and directional vision. SCE presently generates a circuit-specific PSPS de-energization threshold for each circuit that will be in scope for an upcoming event. These de-energization thresholds are created before every event because they take into account the latest information regarding a particular circuit’s condition (e.g., wind-exacerbated maintenance items, load rolls that have affected circuit topology, deployed mitigations like covered conductor installation, etc.). SCE uses this information to guide field patrol resources to verify circuit conditions and provide the latest situational awareness to the Emergency Operations Center before, during and after PSPS events. Please also see Section 8.2.2 in SCE’s 2021 WMP Update which discusses additional variables used to guide PSPS decision making. b) SCE currently generates one PSPS de-energization threshold for each circuit, but seeks to minimize de-energization footprints where possible, should certain isolatable segments not exceed that threshold. Please see Section 8.1.2 in SCE’s 2021 WMP Update that includes PSPS expectations in 2021 and through the plan period. Please also see SCE’s corrective action plan related to its PSPS program pursuant to CPUC President Marybel Batjer’s letter issued January 19, 2021, in R.18-12-005, that will be filed on February 12, 2021. c) As described in Section 8.1.2 in its 2021 WMP Update, SCE plans to assess the feasibility of replacing the current methodology for setting PSPS thresholds and triggers with a dynamic, machine-learning model that derives circuit thresholds and triggers. SCE began the development of this model in 2020 and will perform rigorous analysis and validation in 2021. Assuming final verification and successful side-by-side testing of the new model against SCE’s current algorithm, SCE will gradually integrate this new data model into its situational awareness tools. Once implemented, this new threshold modeling capability should allow SCE to create thresholds for all HFRA circuits based on asset-level data for probabilities of contact from foreign object or equipment failure. | 2021-01-15 | 2021-02-11
CalAdvocates-SCE-2021WMP-01 | 010 | For each program identified in WMP section 5.3, Plan Program Targets: a) Provide the annual program targets from the year 2019 onward as identified in the 2019 WMP filing. b) Provide the annual program targets from the year 2020 onward as identified in the 2020 WMP filing. c) List the actual work completed for 2019. d) List the actual work completed for 2020. | a) SCE’s 2019 wildfire initiative targets were included in its 2019 WMP. Please see SCE’s 2019 WMP at the following link: https://docs.cpuc.ca.gov/PublishedDocs/Efile/G000/M263/K645/263645320.PDF Please also see SCE’s Advice Letter 4153-E that provides the status of end-of-year 2019 WMP initiatives as of the date of the filing. https://www.cpuc.ca.gov/uploadedFiles/CPUCWebsite/Content/News_Room/NewsUpdates/2020/2020_01_31_SCE%20AL%204153-E.pdf Please also see SCE’s 2019 WMP annual compliance report that is attached and was sent to the service list of Rulemaking 18-10-007 on April 1, 2020 and includes final results of SCE’s 2019 WMP initiatives. b) SCE’s 2020 wildfire initiative targets were included in its 2020-2022 WMP. Please see SCE’s 2020-2022 WMP at the following link: https://www.sce.com/sites/default/files/AEM/Wildfire%20Mitigation%20Plan/SCE's%202020-2022%20Wildfire%20Mitigation%20Plan%20-%20Revision%2003.pdf c) Please see SCE’s response to part a) above. d) Please see SCE’s 2021 WMP Update that includes its wildfire initiative work completed in 2020. https://www.sce.com/sites/default/files/AEM/Wildfire%20Mitigation%20Plan/2021/SCE%202021%20WMP%20Update.pdf | 2021-01-15 | 2021-02-11
CalAdvocates-SCE-2021WMP-01 | 011 | For each mitigation initiative identified in WMP section 7.3.1, Financial data on mitigation initiatives: a) Provide the spending forecasts from the year 2019 onward as identified in the 2019 WMP filing. b) Provide the spending forecasts from the year 2020 onward as identified in the 2020 WMP filing. c) Provide the actual spending for 2019. d) Provide the actual spending for 2020. | a) The 2019 forecast spend for wildfire initiatives was included in our 2019 WMP. Please refer to SCE’s response to Question No. 10. b) The 2020 forecast spend for wildfire initiatives was included in our 2020-2022 WMP. Please refer to SCE’s response to Question No. 10 c) The 2019 recorded costs for wildfire initiatives was included in our 2020-2022 WMP. d) Please see SCE’s 2021 WMP Update (Chapter 2) and Table 12 in our Q4 2020 Quarterly Data Report (QDR) that includes our wildfire initiative recorded costs in 2020. | 2021-01-15 | 2021-02-11
CalAdvocates-SCE-2021WMP-01 | 012 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports — conducted by both internal and external entities — that were completed since January 1, 2020 and that examined any programs, initiatives, or strategies described in your 2020 Wildfire Mitigation Plan. External entities include, but are not limited to, contractors, auditors, and Independent Evaluators. | As described in our 2021 WMP Update (See Sections 7.3.4.14 and 7.3.5.13), SCE performs routine Quality Control (QC) of asset and vegetation inspections. Additionally, QC and Quality Assurance (QA) efforts may be ad hoc during a given year. SCE’s response includes a description of these routine and ad hoc QA/QC efforts and the associated complete and final QA/QC reports. SCE’s Transmission & Distribution QA/QC programs are intended to help ensure that inspection activities conform to the requirements of SCE’s inspection programs. A QC inspection is conducted by evaluating the results of completed inspections after the fact. The data from the various QA/QC analysis are used to understand status of programs, help identify challenges and root causes (for example, permitting and customer access challenges for line clearance), and identify issue that need follow-up actions. Actionable findings identified during QC inspections are used for performance scoring to measure the ability of SCE inspectors to accurately identify and classify the potential safety and reliability risks of General Order 95 violations, potential ignition risks, and other safety hazards. All findings identified during the QC review are remediated, and in some instances, corrective actions are initiated. Reports from various QC programs are described below. SCE’s QA programs evaluate the process as opposed to the evaluation of the finished product done by QC reviews. The QA review evaluates the process and supporting evidence to provide reasonable assurance to management that the WMP goals/activities have been met. The QA review can also provide recommendations to improve quality and consistency of data evidence. An example of a QA review is described below. Together, SCE’s QA/QC programs help drive continuous improvement by identifying non-conformances with SCE standards, determining causes of non-conformance, or driving corrective actions to improve performance. The quality program will track action plans to identified corrective actions, which can include changes implemented to inspection processes, training, etc., to continuously improve the inspection programs based on QA/QC findings. In 2020, SCE performed QC of asset inspections for 17,789 transmission, distribution, and generation structures in HFRA (WMP initiative IN-2) to assess the inspections conformance to the requirements of SCE’s overhead inspection programs by evaluating the results of the inspection after-the-fact. This exceeded the target of 15,000 inspections from SCE’s 2020 WMP. The IN-2 initiative was tracked as a WMP goal, with a target to complete 15,000 inspections throughout 2020, and monthly goal updates would report progress towards completion of the annual inspection target. Details regarding overall inspection program findings and quality scores are displayed in an online quality dashboard and reports are provided throughout the year to management. The following charts show the year-end 2020 status and activity for the 2020 WMP IN-2 initiative: SCE also performed QC inspections of other WMP initiatives. These QC activities are displayed in a quality dashboard and program results are typically reported to management monthly. The quality dashboard is an online tool that displays results for various QC programs in a centralized location and is assessable by SCE employees through SCE’s internal web browser. Information displayed on the dashboard includes the number of inspections performed, program conformance rate details, and top findings by category. A conforming structure is one that does not have an actionable finding identified during the quality review or inspection, i.e., the QC inspection matched the previous inspection performed by the inspector. SCE calculates a monthly conformance rate by dividing the count of conforming structures inspected by the count of inspected structures. For example, if 90 structures are found to be conforming out of 100 structures reviewed by quality inspectors, the conformance rate would be 90%. Depending upon the complexity of the structure, there can be several items that can lead to a finding of nonconformance, and only one condition needs to be identified for the structure to be deemed nonconforming. The following screen shots from the quality dashboard show year-end 2020 results for WMP related initiatives regarding distribution Overhead Detailed Inspections (ODI), transmission inspections, generation inspections, distribution Aerial inspections, and the Vegetation Management program. These screen shots represent the type of information that is typically reviewed with program owners and management monthly. Also, attached are reports presented to program managers and/or management that include the QA/QC dashboard information. These attached reports can also contain information beyond QA/QC, including attorney-client privileged information. SCE has redacted material from the reports that is attorney-client privileged/attorney work product. Additionally, and as noted above, SCE may conduct ad hoc QA/QC during a given year. SCE is attaching the following four ad hoc QA/QC reports. The document entitled "2020 TD WMP QA Review" is a status update for a one-time QA review performed in 2020 that examined several 2020 WMP activities. The purpose of this QA review was to evaluate WMP activities and look for potential areas of improvement. The attached copy of that initial status report, was presented to SCE management on October 14, 2020. This report contains staff's preliminary findings. SCE is still reviewing and addressing the potential findings noted in the report. Many of the potential findings identified in this initial report have been resolved or are being actively worked on by SCE. A final report has not been produced. Below are some of the action items SCE has taken or is currently taking to proactively address the potential issues contained identified in the report: • Revisions to questions on the inspection form to reduce the potential for confusion • Drafted revisions to the inspection form to note instances where corrective action is required • Development of a dashboard to monitor distribution ground questions • Development of a Transmission dashboard to monitor questions • Development of training material The document entitled “Covered Conductor Inspections- Results and Next Steps” is a report on an engineering review to validate that installation of covered conductor is conforming to the new SCE Standards. SCE’s engineering team reviewed a sample set of inspections of installed covered conductor. This report contains engineering’s findings and recommendations. SCE has and is addressing the issues found as described in the report. Many of the issues identified in this report have been resolved or are being actively worked on by SCE. Two other documents that may be responsive are QA reviews of documentation to support compliance with NERC’s transmission vegetation management standards, CPUC Resolution ESRB-4 (vegetation management), and Public Resource Codes 4292-4296. Because these requirements involve reviews of vegetation management documentation that may overlap with WMP initiatives, SCE is including them in the attached reports. | 2021-01-15 | 2021-02-17
CalAdvocates-SCE-2021WMP-01 | 013 | Provide an Excel table of all defects in the year 2020 found by the Wildfire Safety Division’s Compliance Branch (as rows) that includes the following information in separate columns. a) Associated Circuit Name b) Defect Type c) Description of defect d) WMP initiative associated with defect e) Date that defect was identified f) Date that defect was corrected g) Priority level of corresponding corrective tag h) Location of defect (latitude/longitude) | Please see the attached Excel file that includes all defects identified by WSD in 2020 and the requested information for items a) through h). | 2021-01-15 | 2021-02-11
CalAdvocates-SCE-2021WMP-02 | 001 | a) How many SCE employees were qualified to perform climbing inspections of transmission towers as of January 1, 2021? b) How many SCE contractors were qualified to perform climbing inspections of transmission towers as of January 1, 2021? c) How frequently are SCE employee climbing inspectors of transmission towers requalified? d) How frequently are SCE contractor climbing inspectors of transmission towers requalified? e) Please respond to questions 1(a) and 1(b) with the appropriate numbers that correspond to January 1 of: a. 2018. b. 2019. c. 2020. | a) SCE’s inspection programs involve ground-based detailed and patrol inspections and aerial inspections. SCE does not have a climbing inspection program. Climbing of transmission towers may occur to perform maintenance or in response to an emergent condition. b - e) See SCE’s response to part a above. | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 002 | a) How many SCE employees were qualified to perform drone inspections of transmission towers as of January 1, 2021? b) How many SCE contractors were qualified to perform drone inspections of transmission towers as of January 1, 2021? c) How frequently are SCE employee drone inspectors of transmission towers requalified? d) How frequently are SCE contractor drone inspectors of transmission towers requalified? e) Please respond to questions 2(a) and 2(b) with the appropriate numbers that correspond to January 1 of: i. 2018. ii. 2019. iii. 2020. | a) Data collection from drone flights are separate from inspections of that data. The aerial inspection program does not utilize SCE employees to perform drone flights. The aerial inspection program uses external drone vendors to capture transmission tower photos. The imagery captured by the drone vendors is then delivered to SCE and inspected by a team of contractors, Qualified Electrical Workers (QEWs) and Engineers. As of January 1, 2021, there are 2 SCE employees qualified to perform transmission inspections. b) The Aerial Inspection Program uses two (2) drone vendors to perform transmission tower photo captures. As of January1, 2021, there are nine (9) contractors qualified to perform transmission inspections of collected images. c) Data collection drone pilots (contractors) are required to obtain a Remote Pilot Certificate from the FAA under the FAA’s Small UAS Rule (Part 107). The SCE employees (QEWs) who are qualified to conduct inspections of transmission towers go through an annual aerial inspection training program. Starting 2021, this training program will be delivered annually, with quarterly refresher trainings. d) Data collection drone vendors undergo a one-time SCE vendor assessment by the Air Operations organization, responsible for aviation safety, prior to starting work for SCE. The vendor is responsible for annual training of Unmanned Aircraft Systems (UAS) personnel. SCE contractors who conduct inspections of transmission towers (QEWs or Engineers) undergo an annual onboarding aerial inspection training program when they start work. SCE holds periodic meetings to review updates or changes to program or inspection requirements. Starting 2021, the contractor QEWs and Engineers will go through an annual training, and a quarterly refresher training throughout the year. e) These questions are answering the number of inspectors, not data collection crews. i. 2018: The Aerial Inspection Program was not established. ii. 2019: (a) average of 5; (b) average of 15. iii. 2020: (a) 2; (b) 9. | 2021-01-22 | 2021-02-15
CalAdvocates-SCE-2021WMP-02 | 003 | a) How many SCE employees were qualified to perform detailed ground inspections of transmission towers as of January 1, 2021? b) How many SCE contractors were qualified to perform detailed ground inspections of transmission towers as of January 1, 2021? c) How frequently are SCE employee detailed ground inspectors of transmission towers requalified? d) How frequently are SCE contractor detailed ground inspectors of transmission towers requalified? e) Please respond to questions 3(a) and 3(b) with the appropriate numbers that correspond to January 1 of: i. 2018. ii. 2019. iii. 2020. | a) As January 1, 2021 SCE had 120 Transmission Linemen (Inspectors) to climb Transmission towers. Climbing Transmission towers are only conducted for maintenance activities and hurt personnel rescue when required. b) SCE does not use contractors to perform detailed ground inspections. c) SCE Linemen (inspectors) are requalified on an annual basis to climb Transmission towers for hurt personnel rescue and to conduct maintenance activities as necessary. d) SCE does not use contractors to perform detailed ground inspections. e) i. 2018 - Approx.: 135 as in 2019 ii. 2019 - 135 iii. 2020 - 120 | 2021-01-22 | 2021-02-15
CalAdvocates-SCE-2021WMP-02 | 004 | Please provide the following: a) The average amount of person-hours to perform a single climbing inspection of a transmission tower in 2020. b) The minimum amount of person-hours spent on a single climbing inspection of a transmission tower in 2020. c) The total amount of person-hours spent on climbing inspections of transmission towers in 2020. d) The total number of transmission towers that SCE performed climbing inspections on in 2020. e) The total number of climbing inspections of transmission towers performed in 2020. f) Please respond to questions 4(a) through 4(e) for: i. 2018. ii. 2019. | Please see SCE’s response to Question No. 1. | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 005 | Please provide the following: a) The average amount of person-hours to perform a single drone inspection of a transmission tower in 2020. b) The minimum amount of person-hours spent on a single drone inspection of a transmission tower in 2020. c) The total amount of person-hours spent on drone inspections of transmission towers in 2020. d) The total number of transmission towers that SCE performed drone inspections on in 2020. e) The total number of drone inspections of transmission towers performed in 2020. f) Please respond to questions 5(a) through 5(e) for: i. 2018. ii. 2019. | Data collection from drone flights are separate from inspections of that data. The aerial inspection program does not utilize SCE employees to perform drone flights. The aerial inspection program uses external drone vendors to capture transmission tower photos using drones. Once the imagery is captured, the images are delivered to SCE and inspected by a team of Qualified Electrical Workers (QEWs) and Engineers. a) On an average, it takes 45 minutes to complete a single inspection of a transmission tower. This process is separate from flying the drone and capturing the images. The average amount of person-hours to capture transmission tower images in 2020 was ~45 minutes. b) The minimum number of person-hours spent on a single inspection of a transmission tower in 2020 is ~ 30 minutes. This process is separate from flying the drone and capturing the images. The minimum number of person-hours spent to capture transmission tower images in 2020 was ~15 minutes. c) The total number of person-hours spent on inspections of a transmission towers in 2020 is ~ 8,477. The total amount of person-hours spent by drone vendors to capture transmission towers in 2020 was ~7,500 hours. d) The total number of transmission assets on which SCE performed inspections in 2020 was 31,667 structures, out of which ~9,241 were towers. The inspection process is separate from flying drones and capturing images. e) The total number of transmission structures one which SCE performed inspections in 2020 was 31,667, out of which ~9,241 were towers. The inspection process is separate from flying drones and capturing images. f) i. 2018: The Aerial Inspection Program was not established. ii. 2019: 5(a)~1 hour for both data capture and inspection; 5(b) ~15 min for data capture and ~30 minutes for inspection; 5(c) ~3,713 hours for inspections; 5(d) ~3,713 inspections; 5(e) ~3,713 inspections | 2021-01-22 | 2021-02-15
CalAdvocates-SCE-2021WMP-02 | 006 | Please provide the following: a) The average amount of person-hours to perform a single detailed ground inspection of a transmission tower in 2020. b) The minimum amount of person-hours spent on a single detailed ground inspection of a transmission tower in 2020. c) The total amount of person-hours spent on detailed ground inspections of transmission towers in 2020. d) The total number of transmission towers that SCE performed detailed ground inspections on in 2020. e) The total number of detailed ground inspections of transmission towers performed in 2020. f) Please respond to questions 6(a) through 6(e) for: i. 2018. ii. 2019. | a) Inspections of a Transmission Tower in HFRA on average takes approximately 0.5 hrs. (30 mins). This excludes any travel time to the Transmission Tower location. b) The minimum amount of time spent on a Transmission Tower in HFRA is approximately 0.3 hrs. (20 mins). This excludes any travel to Transmission Tower locations. c) The total amount of person hours spent in 2020 to conduct detailed inspections on Transmission Towers in HFRA was approximately 4,936 hours. d) The total number of Transmission Towers in HFRA inspected during 2020 was 9,872. e) The total number of Transmission Towers in HFRA inspected during 2020 was 9,872 (same response as d). f) i. 2018. N/A. In 2018 Tower Inspection information was captured at the circuit and not the structure level, which differs from the structure-level approach in 2019 & 2020. ii. 2019 (a) to (e). 2019 inspected towers are approximately the same values as in 2020 within the HFRA boundaries. | 2021-01-22 | 2021-02-15
CalAdvocates-SCE-2021WMP-02 | 007 | a) How many Level 1 corrective tags were issued as a result of transmission tower climbing inspections in 2020? b) How many Level 2 corrective tags were issued as a result of transmission tower climbing inspections in 2020? c) Please respond to questions 7(a) through 7(b) for: i. 2018. ii. 2019. | a) As noted in response to Question 1, SCE’s inspection programs involve ground-based detailed and patrol inspections and aerial inspections. SCE does not have a climbing inspection program. b) See response to part a. c) See response to part a | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 008 | a) How many Level 1 corrective tags were issued as a result of transmission tower drone inspections in 2020? b) How many Level 2 corrective tags were issued as a result of transmission tower drone inspections in 2020? c) Please respond to questions 8(a) through 8(b) for: i. 2018. ii. 2019. | SCE’s aerial program was launched in 2019 and does not differentiate if a repair notification was captured from a helicopter or a drone. The table, below, contains pending and completed repair notifications identified in SCE’s system of record on a tower as the result of an aerial inspection. Table | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 009 | a) How many Level 1 corrective tags were issued as a result of transmission tower detailed ground inspections in 2020? b) How many Level 2 corrective tags were issued as a result of transmission tower detailed ground inspections in 2020? c) Please respond to questions 9(a) through 9(b) for: i. 2018. ii. 2019. | The table, below, contains pending and completed repair notifications in SCE’s system of record that were found during either a transmission ground patrol or a transmission risk-informed inspection. | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 010 | a) How many Level 1 corrective tags were issued as a result of work verification or quality control of transmission tower climbing inspections in 2020? b) How many Level 2 corrective tags were issued as a result of work verification or quality control of transmission tower climbing inspections in 2020? c) Please respond to questions 10(a) through 10(b) for: i. 2018. ii. 2019. | a) Please see SCE’s response to Question No. 1 that informs how SCE’s inspection programs do not include climbing inspections. b) Please see the response to part a. c) Please see the response to part a. i. N/A ii. N/A | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 011 | a) How many Level 1 corrective tags were issued as a result of work verification or quality control of transmission tower drone inspections in 2020? b) How many Level 2 corrective tags were issued as a result of work verification or quality control of transmission tower drone inspections in 2020? c) Please respond to questions 11(a) through 11(b) for: i. 2018. ii. 2019. | a) SCE’s Transmission & Distribution Quality organization did not perform quality control reviews of transmission tower drone inspections from 2018 to 2020. b) Please see the response to part a. c) Please see the response to part a. i. N/A ii. N/A | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 012 | a) How many Level 1 corrective tags were issued as a result of work verification or quality control of transmission tower detailed ground inspections in 2020? b) How many Level 2 corrective tags were issued as a result of work verification or quality control of transmission tower detailed ground inspections in 2020? c) Please respond to questions 12(a) through 12(b) for: i. 2018. ii. 2019. | a) SCE’s T&D Quality organization performed 42 quality control (QC) inspections on transmission tower detailed ground inspections in 2019, and 67 QC inspections on transmission tower detailed ground inspections in 2020. No Priority 1 or Priority 2 conditions were identified during these QC inspections in 2019 or 2020. No QC inspections were performed on transmission tower detailed ground inspections in 2018. b) Please see the response to Question 12.a of this data request. c) Please see the response to Question 12.a of this data request. i. N/A ii. N/A | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-02 | 013 | Please provide: a) All current training materials that SCE uses to train inspectors1 for transmission tower inspections.2 b) All current guidelines, protocols, and checklists that SCE directs its inspectors to use for transmission tower inspections. | a) See attached Transmission Training Materials for ground transmission towers (TOCI v2021 Condition Assessment Survey123 user guide). b) See attached Transmission Checklist (Transmission Condition Assessment Form). | 2021-01-22 | 2021-02-15
CalAdvocates-SCE-2021WMP-02 | 014 | Provide an Excel table of all Level 1 and Level 2 corrective tags issued from January 1, 2018 to December 31, 2020 (as rows) that includes the following information in separate columns: a) Corrective Tag ID. b) Circuit Name. c) Priority Level (1 or 2). d) Date corrective tag was issued. e) Required completion date of corrective tag. f) Date corrective tag was completed or resolved. | The attached Excel document entitled “Tower-Notifications.xlsx,” contains all pending and completed priority 1 and 2 repair notifications found between January 1, 2018 and December 31, 2020. | 2021-01-22 | 2021-02-12
CalAdvocates-SCE-2021WMP-03 | 001 | The following questions relate to SCE’s Quarterly Data Reports associated with its Wildfire Mitigation Plan (WMP). For each of the following categories of WMP-related events and mitigation work listed below, state whether SCE has provided geospatial data to the Wildfire Safety Division covering the first and second quarters of 2020, and if so, the date when SCE provided the data. a) Outages b) Utility-related Ignitions c) Mitigation work completed for each WMP initiative | a) SCE did not provide first or second quarter 2020 outage data. b) SCE did not provide first or second quarter 2020 ignition data. c) In accordance with the Quarterly Report requirements for the September 9, 2020 Quarterly Report GIS submission, SCE provided the WMP initiative data available to us at that time. The available WMP initiative data layers and tables SCE provided in the September 9, 2020 submission are detailed below. SCE_20200909.gdb SCE_Initiative SCE_VegetationManagementInspectionPoint_20200909 SCE_VegetationManagementInspectionLog_20200909 SCE_VegetationManagementProjectPoint_20200909 SCE_VegetationManagementProjectPolygon_20200909 SCE_VegetationManagementProjectLog_20200909 SCE_AssetInspectionLine_20200909 SCE_AssetInspectionPoint_20200909 SCE_InitiativeAssetLog_20200909 SCE_GridHardeningLine_20200909 SCE_GridHardeningPoint_20200909 SCE_GridHardeningLog_20200909 | 2021-02-11 | 2021-02-17
CalAdvocates-SCE-2021WMP-03 | 002 | The following questions relate to SCE’s Quarterly Data Reports associated with its Wildfire Mitigation Plan (WMP). Provide GIS data covering January 1, 2020 through June 30, 2020 for all feature classes and tables, except for the classes and tables listed below, that SCE included in its February 5, 2021 Quarterly Data Report. Provide that data using the same geodatabase template that SCE used in filing its February 5, 2021 Quarterly Data Report. a) SCE_PrimaryDistributionLine b) SCE_SecondaryDistributionLine c) SCE_TransmissionLine d) SCE_CustomerMeter e) SCE_Substation f) SCE_TransformerSite g) SCE_TransformerDetail | The feature classes listed below represent a subset of the data provided by SCE in its Feb. 5, 2021 Quarterly Data Report (QDR) submission (some of which designated confidential--please refer to the previously provided confidentiality declaration) and are included in the attached zip files. The remaining requested data that SCE provided in its Feb. 5, 2021 QDR (i.e., not listed below) are not included in this data delivery. These omitted feature classes and tables contain data for only the date range Oct. 1 through Dec. 31, 2020. To obtain geospatial data for the Jan. 1 to June 30, 2020 timeframe for these omitted feature classes would require a new work effort similar to the production of geospatial data provided from Oct. 1 through Dec. 31, 2020. This is a one- to two-month process because the data is in many source systems, does not reside in SCE’s GIS, would need to be extracted, correlated, and compiled into new datasets, loaded into GIS within the WSD’s GIS Schema requirements, and then reviewed for accuracy/compliance with the requirements. Additionally, the WSD issued new GIS Schema Requirements on Feb. 4, 2020 which SCE is still reviewing. SCE can provide this information on May 1, 2020 contemporaneously with its next QDR submittal but recommends using the WSD’s new GIS Schema requirements consistent with requirements for the May 1, 2020 QDR submittal. SCE_20210205_NonConfidential.gdb SCE_AssetPoint SCE_Camera_20210205 SCE_WeatherStation_20210205 SCE_OtherRequiredData SCE_AdministrativeArea_20210205 SCE_RedFlagWarningDayPolygon_20210205 SCE_20210205_Confidential.gdb SCE_AssetPoint SCE_ConnectionDevice_20210205 SCE_Fuse_20210205 SCE_SupportStructure_20210205 SCE_Switchgear_20210205 SCE_Initiative SCE_GridHardeningLine_20210205 SCE_GridHardeningPoint_20210205 SCE_GridHardeningLog_20210205 SCE_OtherRequiredData SCE_CriticalFacility_20210205 SCE_OtherPowerLineConnectionLocation_20210205 CONFIDENTIAL | 2021-02-11 | 2021-02-17
MGRA-SCE-003 | 006 | Regarding the use of the Technosylva fire spread model and its used to calculate wildfire consequences: What is the maximum duration in hours simulated used to model maximal losses using the Technosylva model? | Wildfire consequences are calculated based on the spread of a fire over an eight (8) hour period for each ignition point. Fire spread predictions are run for each of the 41 weather scenarios extracted from the SCE 20-year climatology. This results in 41 different risk values for each variable (acres, structures, population) for each ignition point. | 2021-02-17 | 2021-02-19
MGRA-SCE-003 | 007 | Regarding the use of the Technosylva fire spread model and its used to calculate wildfire consequences: What is the average size of “maximal” wildfire spread in acres when the Technosylva model is run to its maximum duration? | The average maximum consequence value in terms of acres impacted for all facility locations (FLOCS) over an eight (8) hour simulation period is 540.496 acres. | 2021-02-17 | 2021-02-19
MGRA-SCE-003 | 008 | Regarding the use of the Technosylva fire spread model and its used to calculate wildfire consequences: What is the typical computational time for a Technosylva run of “maximum” duration? Include assumptions regarding CPU type, speed and memory consumed | Wildfire consequences are calculated based on the spread of a fire over an eight (8) hour period predicted for each ignition point. Fire spread predictions are run for each of the 41 weather scenarios extracted from the SCE 20-year climatology. This results in 41 different risk values for each variable (acres, structures, population) for each ignition point. This results in approximately 29 million simulations. This data is computed in a cloud environment by SCE’s vendor (Technosylva). A single simulation can be run on a typical laptop computer with eight (8) gigabytes of RAM from anywhere between approximately 30 seconds to 2 minutes. | 2021-02-17 | 2021-02-19
MGRA-SCE-003 | 009 | Regarding the use of the Technosylva fire spread model and its used to calculate wildfire consequences: Have Technosylva fire spread simulations been run for 24 and 48 hour propagation times? If yes, how do the results compare to the results of 8 hour simulations in terms of average acres impacted and in terms of computing resources? If not, why has this not been performed? | SCE does not possess fire spread simulations with 24- or 48-hour propagation times. A standard eight (8) hour duration is chosen as a consistent duration for each simulation to allow for comparison and interpretation of outputs when comparing all simulations. | 2021-02-17 | 2021-02-21
CalAdvocates-SCE-2021WMP-04 | 001 | On page 47 of your WMP, you state that “SCE uses 41 weather scenarios across a 20-year historical climatology in its WRRM consequence model.” Provide a list of the attributes (e.g., wind speed, atmospheric humidity) that are used to differentiate those scenarios from each other. | The variables used for each weather scenario for each 2-kilometer x 2-kilometer grid are: • Wind speed and direction (hourly) • Temperature (hourly) • Relative Humidity (RH) (hourly) • Dead fuel moisture (1 hour, 10-hour, 100-hour) • Herbaceous live fuel moisture (changes daily) • Woody live fuel moisture (changes daily) | 2021-02-16 | 2021-02-19
CalAdvocates-SCE-2021WMP-04 | 002 | a) What is the duration of the weather scenarios used in the WRRM consequence model? b) In these weather scenarios, do the attributes evolve over the duration of the scenario (for example, if the weather scenario lasts 48 hours, temperature and wind speed would rise and fall over the course of the 48-hour period)? | a. Wildfire consequences are calculated based on the spread of a fire over an eight (8) hour period for each ignition point. Fire spread predictions are run for each of the 41 weather scenarios extracted from the SCE 20-year climatology. This results in 41 different risk values for each variable (acres, structures, population) for each ignition point. SCE utilizes the maximum fire consequences predicted out of the 41 scenarios for each individual ignition point over an eight (8) hour burn period. Use of a consistent duration for each simulation allows for comparison and interpretation of outputs when comparing all simulations. | 2021-02-16 | 2021-02-19
CalAdvocates-SCE-2021WMP-04 | 003 | In analyzing the fire consequence outputs of the 41 weather scenarios used in your WRRM, does SCE prioritize mitigation work by: (a) comparing the maximum asset-level fire consequence out of the 41 scenarios for each individual asset, (b) comparing asset-level fire consequences in the scenario that produced the greatest consequence for SCE’s service territory as a whole, or (c) using some other criteria? If the answer is (c), please explain how SCE uses the fire consequence outputs from the 41 weather scenarios in SCE’s prioritization decisions. | Wildfire consequences are calculated based on the spread of a fire over an eight (8) hour period for each ignition point. Fire spread predictions are run for each of the 41 weather scenarios extracted from the SCE 20-year climatology. This results in 41 different risk values for each variable (acres, structures, population) for each ignition point. SCE utilizes the maximum fire consequences predicted out of the 41 scenarios for each individual ignition point over an eight (8) hour burn period as a component of the prioritization process, which is similar to the methodology described in (a). | 2021-02-16 | 2021-02-22
CalAdvocates-SCE-2021WMP-04 | 004 | For the following structure:  Support Structure ID: 4869798E (Wood Pole, Lat/Long: 34.47843933105469, - 118.68360900878906) Provide inputs and outputs of the WRRM as follows: a) A list of the inputs that are used for determining the Probability of Ignition (POI). b) A list of the inputs that are used for determining the wildfire consequence. c) The Probability of Ignition (POI) rating generated by the WRRM. d) The wildfire consequence outputs generated by the WRRM for the same weather scenario used in 5(c). If applicable, provide inputs and outputs at the equipment level and pole/tower level. | a) The inputs to SCE’s POI models include the following: Table b) List of input to the consequence models include: Surface Fuels; Canopy Fuels; Weather Data; Live/Dead Fuel Moisture Data; Building/Structure Data; Population Data; SCE Assets. c) The POI for this structure is 0.0002193877. d) The wildfire consequence for this structure is 47629.3406199072 (Edison understands "5(c)” to refer to “4(c)”) | 2021-02-16 | 2021-02-21
CalAdvocates-SCE-2021WMP-04 | 005 | For the following structure:  Support Structure ID: 1922561E (Light Weight Steel Pole, Lat/Long: 34.798240661621094, -118.74307250976562) Provide inputs and outputs of the WRRM as follows: a) A list of the inputs that are used for determining the Probability of Ignition (POI). b) A list of the inputs that are used for determining the wildfire consequence. c) The Probability of Ignition (POI) rating generated by the WRRM . d) The wildfire consequence outputs generated by the WRRM for the same weather scenario used in 6(c). | a) The inputs to SCE’s POI models include the following: Table b) List of input to the consequence models include: Surface Fuels; Canopy Fuels; Weather Data; Live/Dead Fuel Moisture Data; Building/Structure Data; Population Data; SCE Assets. c) The POI for this structure is 0.00013524958. d) The wildfire consequence for this structure is 3080.27856445312 (SCE is not clear with respect to the reference in the question to “6(c)”). | 2021-02-16 | 2021-02-22
CalAdvocates-SCE-2021WMP-04 | 006 | Regarding your response to CalAdvocates-SCE-2021WMP-01, Question 4, one of the rows is labelled as “Other”. That row accounts for 4077.44 total circuit miles and a risk score of approximately 1,546,868. What distribution lines are included in the “Other” category? | SCE’s risk models were created at FLOC (Functional Location: structure like a pole) level. Some FLOCs in our database do not have a circuit association because the system used for reporting data does not have circuit name information unless a FLOC also has other equipment (such as a transformer) attached. Therefore, we cannot provide a precise listing of circuits included in the other category. This does not reduce our ability to prioritize risk as we know that the FLOC exists and know the physical location and risk score of the FLOC. For prioritizations done at the circuit-segment level such as covered conductor, FLOC level detail is not needed as risk scores are calculated at the segment level. | 2021-02-16 | 2021-02-21
TURN-SCE-001 | 001 | Re SCE Excel data attachment, Table 2, subpart 7 (“Number of ignitions”) and sub-parts: a. Please confirm that SCE has included all CPUC reportable ignitions in this data set. b. If SCE has not included all ignitions, please re-produce all rows of #7 (7a- 7d) in Excel to include all reportable ignitions in each year for each category. c. Please provide the CPUC reportable ignition database, including all columns and rows, which part (b) is based on. | a) The data in Table 2, subpart 7, contains all CPUC reportable ignitions for 2015 to 2019 that SCE submitted pursuant to CPUC D. 14-02-015. The ignition data for 2020 includes all ignitions SCE plans to submit for events that occurred in 2020 as required by D. 14-02-015. b) See above. c) See above. | 2021-02-17 | 2021-02-21
TURN-SCE-001 | 002 | Please provide the activity name and total costs forecast for each activity for 2020-2022, annually, that SCE expects to record to memorandum accounts. Please explain and quantify whether SCE will record any amounts from activities authorized in its GRC to memorandum accounts. | The recorded (2020) and forecast (2021-2022) costs for SCE’s wildfire initiatives are included in Table 12 (Excel) submitted as part of SCE’s Q4 2020 Quarterly Data Report (and in pdf in Appendix 9.7 of SCE’s 2021 WMP Update). Additionally, Tables 3-1 and 3-2 in our 2021 WMP Update includes summary costs by program area and the total of our wildfire initiatives. Table 12, pursuant to the WSD’s requirements, also includes recorded and forecast costs for non-wildfire work. SCE is attaching an Excel file with just Table 12 that includes added filters and color coding to help clarify the differences with the costs in this table and Tables 3-1 and 3-2. Please see the instructions below: • If you filter column O (“If new: memorandum account”) to de-select “NA” and “(Blanks)” (leaving only what is in our balancing/memo accounts) and sum up the dollars in rows U&V (2020), Y&Z (2021) and AC&AD (2022), it will add up to what is in Tables 3-1 and 3-2. To help illustrate this, we highlighted in yellow the filtered fields of columns O, U, V, Y, Z, AC and AD. So, the highlighted fields add up to the totals in Tables 3-1 and 3-2. • We also highlighted all of the non-wildfire rows in red text. These are all rows that either 1) have no costs; or 2) are costs we included for programs we consider general/routine operations. Please note that for most of these, we included costs for the entire service area, and not just HFRA, because that is how our operating plans are structured - this is noted in the column T notes, where applicable. For 2020, relevant costs have been recorded in the Wildfire Mitigation Memorandum Account (WMPMA), the Fire Risk Mitigation Memorandum Account (FRRMA), the Fire Hazard Prevention Memorandum Account (FHPMA), and the Grid Safety and Resiliency Balancing Account (GSRPBA) (collectively, the Fire Risk Mitigation Memorandum Accounts), pursuant to Commission decisions and the Public Utilities Code. In SCE’s 2021 GRC Track 1, SCE has proposed a two-way Wildfire Risk Mitigation Balancing Account (WRMBA) and a two-way Vegetation Management Balancing Account (VMBA). If the WRMBA and VMBA are approved by the Commission, SCE will record all 2021 and 2022 costs associated with its WMP programs and activities in one of those two accounts, as appropriate. If the WRMBA and/or VMBA are not approved in the form as proposed by SCE in the GRC, SCE will continue to record applicable WMP-related costs in the Fire Risk Mitigation Memorandum Accounts to the extent necessary. | 2021-02-17 | 2021-02-22
WSD-SCE-001 | 001 | The WSD requests clarification of two (2) overarching issues regarding the 2021 WMP Update Table 12 (initiative spend by WMP activity), as follows: Split reported spend by activity in HFTD and total activity spend (i.e., territory-wide including in non-HFTD) • Separate the spend in Risk assessment and mapping activities from “General operations” and “Situational awareness” such that the allocated spend to Risk assessment and mapping is greater than 0. Risk assessment and mapping activities are in rows 9-13 and are highlighted in tan across all columns from G through BP. Provide this updated information in the same MS Excel file described above. | Please see attached spreadsheet, entitled “WSD-SCE-001 Q1 Data request SCE 2021 Table 12_v02 20210223.” | 2021-02-18 | 2021-02-23
WSD-SCE-001 | 002 | The WSD requests clarification of two (2) overarching issues regarding the 2021 WMP Update Table 12 (initiative spend by WMP activity), as follows: Given changes in WMP activity spending, report planned spend as detailed in the 2020 WMP under the reporting system of the 2021 WMP (i.e., activity spend in HFTD and territory-wide) | Please see the attached Excel file entitled “Data request SCE 2021 Table 12_20210223.” | 2021-02-18 | 2021-02-23
WSD-SCE-001 | 003 | For all activities listed under “Vegetation Management and Inspections” (i.e., rows 61-82), which incurred programmatic cost increases (i.e., not attributable to increases form reporting non-HFTD area spend) from those reported in the 2020 WMP, provide the following: o An explanation for the cost increase o A breakdown of the increased amount attributed to changes in activity scope, labor costs, etc. | Vegetation Management program cost increases from 2020 WMP to 2021 WMP include:  Technology Solutions: Increase due to new Arbora Technology Tool investment, emergent program post-2020 WMP ($16M).  Hazard Tree Removal: Increase in forecast driven by inclusion of SB 247 and related rate increases, inclusion of Palm Program ($10M).  Veg Mgmt: Line Clearing: Increase in forecast driven by: o Inclusion of SB 247 and related rate increases ($135M annually) unknown at the time of filing of the 2020 WMP. o Inclusion of the Dead & Dying Tree Removal Program ($45M annually), for which costs were not included in SCE’s 2020 WMP wildfire initiatives. SCE’s Dead & Dying Tree Removal Program has been in existence since 2014. It was initiated as a result of Governor Brown’s declaration of a state of emergency regarding drought mitigation in Resolution ESRB-4. SCE began taking measures to increase vegetation inspections and remove hazardous, dead, and sick trees and other vegetation near our power lines and poles. o Cost increases for more first-time expanded clearances (estimated at $15M annually) initiated as part of D.17-12-024 to increase recommended clearance distances at the time of trimming in HFRA. | 2021-02-18 | 2021-02-23
CalAdvocates-SCE-2021WMP-05 | 003 | Provide all available workpapers supporting the calculation of the rate and bill impacts shown in Table 3-3 on p.31-32 of SCE’s 2021 Wildfire Mitigation Plan Update. | See attached confidential and non-confidential files for the rate and bill impact calculations shown in Table 3-3. CONFIDENTIAL | 2021-02-18 | 2021-02-22
CalAdvocates-SCE-2021WMP-05 | 004 | Does SCE have a copy of the Institute of Electrical and Electronics Engineers (IEEE) standard called "C37.230-2020 - IEEE Approved Draft Guide for Protective Relay Applications to Distribution Lines" (https://standards.ieee.org/standard/C37_230-2020.html)? If so, please provide a copy. (The Public Advocates Office understands that the document may be deemed confidential.) | SCE does have a copy of Institute of Electrical and Electronics Engineers (IEEE) standard called "C37.230-2020 - IEEE Approved Draft Guide for Protective Relay Applications to Distribution Lines" (Standard). However, SCE is not permitted to share the Standard without license from the provider. SCE is seeking permission to provide the Standard and will serve it in a supplementary response if SCE receives permission to do so. | 2021-02-18 | 2021-02-23
TURN-SCE-002 | 001 | Re SCE Excel data attachment, Table 12, initiative 7.3.3.3.1 (Covered conductor installation): a. The table specifies that if an alternative unit is used, “still required to report line miles,” but SCE did not report line miles for this initiative. If possible, please provide the number in line miles actual and projected for each year 2020-2022. b. Please explain how SCE converts from “# of miles of covered conductor installs” to “line miles.” Provide a sample calculation. Provide an estimate of the standard of deviation if there is variance. | a. SCE reported the number of miles of covered conductor installs in circuit miles as an alternative unit because line miles are not utilized by SCE as part of the developed risk models or as a criterion for targets. Additionally, SCE has not been required to report out in line miles; therefore, our current GIS systems data inputs limit us from providing this information. b. The WSD defines circuit miles and line miles as follows:1 • Circuit Miles: The total length in miles of separate circuits regardless of the number of conductors used per circuit. • Line Miles: The number of miles of transmission and/or distribution line. Differs from circuit miles because individual circuits, such as the two circuits of a double-circuit line, are not counted separately in circuit miles but are counted as separate total miles of line. SCE found the definitions for “Circuit Miles” and “Line Miles” to be in conflict. The definition for circuit miles specifically states, “the total length of separate circuits,” while the last portion of the definition for line miles states “as the two circuits of a double-circuit line, are not counted separately in circuit miles but are counted as separate total miles of line.” The former states the length is counted for each circuit (even if the circuit runs along the same path), while the latter does not count the lengths when the circuit runs along the same path. 1 Wildfire Safety Division (November 2020). Resolution WSD-011 – Attachment 2.2: 2021 Wildfire Mitigation Plan (WMP) Guidelines Template, retrieved February 23, 2020 from https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M352/K460/352460864.pdf Due to this conflict, SCE used its definition for circuit versus line miles: • “Circuit Miles” are the total linear miles considering all circuits along the path of reconductor. o For example, if Circuit X is getting reconductored from point A to point B for 1 mile, and Circuit Y runs along the same path and will be reconductored as well, the total Circuit Miles would be equal to 2 Circuit Miles. • “Line Miles” are the linear path of reconductor as a distance from point A to point B regardless of the number of circuits. o For example, if Circuit X is getting reconductored from point A to point B for 1 mile, and Circuit Y runs along the same path and will be reconductored as well, the total Line Miles would equal to 1 Line Mile. Under SCE’s definition, the process to convert the number of covered conductor installs to line miles would be overly burdensome. The process would consist of verifying all portions of reconductor at the project level to verify locations where circuits run along the same path and by mapping each asset to circuits to which the asset is connected. This process would require an extensive manual effort due to the current limitations of GIS data. | 2021-02-19 | 2021-02-24
TURN-SCE-002 | 002 | Re SCE Excel data attachment, Table 12, initiative 7.3.3.6 (Distribution pole replacement): a. The table specifies that if an alternative unit is used, “still required to report line miles,” but SCE did not report line miles for this initiative. If possible, please provide the number in line miles actual and projected for each year 2020-2022. b. Please explain how SCE converts from “# of pole remediations” to “line miles.” Provide a sample calculation. Provide an estimate of the standard of deviation if there is variance. | a. SCE reported the counts of poles remediated as an alternative unit because line miles are not an applicable measurement for pole remediations. Pole remediations represents a replacement of a single asset, which is a single point, versus a distance which is typically measured by circuit or line miles. b. The WSD defines circuit miles and line miles as follows:1  Circuit Miles: The total length in miles of separate circuits regardless of the number of conductors used per circuit  Line Miles: The number of miles of transmission and/or distribution line. Differs from “circuit miles” because individual circuits, such as the two circuits of a double-circuit line, are not counted separately in circuit miles but are counted as separate total miles of line. SCE found the definitions for “Circuit Miles” and “Line Miles” to be in conflict. The definition for circuit miles specifically states “the total length of separate circuits,” while the last portion of the definition for line miles states “as the two circuits of a double-circuit line, are not counted separately in circuit miles but are counted as separate total miles of line.” The former states the length is counted for each circuit (even if circuits run along the same path), while the latter does not count the lengths when circuits run along the same path for a circuit mile. 1 Wildfire Safety Division (November 2020). Resolution WSD-011 – Attachment 2.2: 2021 Wildfire Mitigation Plan (WMP) Guidelines Template, retrieved February 23, 2020 from https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M352/K460/352460864.pdf Due to this conflict, SCE used its definition for circuit versus line miles: o Circuit Miles are the total linear miles considering all circuits along the path of reconductor. o Line Miles are the linear path of reconductor as a distance from point A to point B regardless of the number of circuits. While SCE does not believe reporting pole remediations in line miles is applicable, under SCE’s definition, the process to convert pole remediations to line miles would be overly burdensome. The process would consist of two parts: 1. Translate the pole remediation into circuit miles; and 2. Verify all portions of circuit miles where there are multiple circuits running along the same path, in order to ensure the length is only counted once in the line mile calculation. The first step of translating the data to circuit miles can be completed by the following equation:  # poles remediated x average span lengths between poles Where the average span lengths will be calculated using asset data counts and GIS circuit mileage information. Currently, the second step would require an extensive manual process due to current limitations of GIS data. This manual process would involve mapping each asset to circuits to which the asset is connected and verifying the locations where multiple circuits run along the same path. | 2021-02-19 | 2021-02-24
CalAdvocates-SCE-2021WMP-06 | 001 | Provide an ESRI geodatabase file of all the approximately 2,700 Grids, as polygon features, that you use to facilitate vegetation management work.1 Provide the following information as attributes for each Grid: a) ID number b) WRRM output(s). If SCE uses multiple types of WRRM outputs for each Grid, provide each type of WRRM output as a separate attribute. | CONFIDENTIAL a. Please see attached: CONFIDENTIAL_CalAdvocates_SCE_2021WMP_06_Question1.gdb.zip (geodatabase zip file)The file contains Featureclasses: •SCE_VegetationManagement_PlanningGrids (1943 grid polygons) •VM_Planning_TransmissionLines (1042 circuits) b.WRRM outputs were not used for SCE’s 2021 work scheduling process, and therefore are notprovided. As stated on page 257 of SCE’s WMP, SCE schedules higher risk HFRA locations forinspection months leading up to peak fire season, to the extent that resources are available and it isfeasible to schedule the work during this time period. This prioritization includes consultation withSCE’s fire scientist and their most current fire risk analysis (which considers fuel and weatherconditions including vegetation density, wind, precipitation, and fire history/activity). However,integration of SCE’s WRRM model into scheduling for SCE’s grids/polygons/circuits is notanticipated to be complete and implemented until the 2022 schedule. SCE’s currentgrid/polygon/circuit count for Distribution and Transmission is 2985. | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 002 | Regarding the Weather Station to Circuit Mapping Project, SCE stated that “The project involves conducting a statistical proximity analysis for the correlation between observed and forecasted sustained windspeed and wind gusts, number of times circuits have reached PSPS criteria in the past, and ability to sectionalize. Each station is ranked by circuit according to the statistical analysis results.” 2 Provide a list in Excel format of the weather stations that have been ranked. Provide each station as a row. As columns, please provide: a) the weather station name, b) station ID, and c) the statistical analysis results used to rank the weather stations. | Please see attached Excel file entitled “Station to Circuit Mapping Data Request.” | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 003 | Regarding the Weather Station to Circuit Mapping Project, in which SCE ranked weather stations according to statistical analysis results,3 provide a narrative description of each kind of statistical analysis result identified (in the response to Question 2(c) above). | 1. Column D and E: station_circuit_wind_corr and station_circuit_gust_corr: • Description: Wind speed and gust correlation between the station’s closest WRF grid cell and circuit level WRF data o Answers the question, from a modeling perspective, can this grid cell approximate circuit level winds? 2. Column F and G: wrf_obs_wind_corr and wrf_obs_gust_corr: • Description: Wind speed and gust correlation between the station’s closest WRF grid cell and observations. o Answers the questions, does WRF validate well at the station? Is there a station siting issue? 3. Column H and I: wind_MAE and gust_MAE: • Description: The Mean Absolute Error. o Model evaluation metric 4. Column J and K: wind_RMSE and gust_RMSE: • Description: The Root Mean Square Error. o Model evaluation metric 5. Column L and M: mean_corr and min_corr: • Description: mean and min value from the correlations listed above in columns D through G | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 004 | Has SCE developed any reports showing which weather stations are most representative of specific circuits?4 If so, provide such report(s). If SCE has not developed such a report, when does it anticipate that such a report will be complete? | Yes, please refer to the attachments. | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 005 | Provide an ESRI geodatabase file of the 17 Areas of Concern (AOC) identified by SCE in its 2021 WMP,5 as polygon features. Include the following as attributes for each feature: a) ID number b) WRRM output(s). If SCE uses multiple types of WRRM outputs for each Grid, provide each type of WRRM output as a separate attribute. | Please see the attached files for SCE’s response. CONFIDENTIAL | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 006 | Identify all independent media sources (including news stations and any channels on which SCE purchased an advertising time slot) that SCE used in 2020 to advertise its Customer and Community Resiliency Programs or the availability of Customer Resiliency Equipment. | For our Critical Care Backup Battery (CCBB) Program which provided a free backup battery to critical care customers, SCE did not purchase any paid media sources. The CCBB Program was marketed through direct mail and emails. PSPS rebates for electric power stations ($50 rebate) and power generators for well water pumping ($300 and $500 rebates) were marketed through direct mail, paid search and social media. A pilot paid search campaign was conducted from July 14 to August 12, 2020, which resulted in 135,476 impressions, a Click Through Rate (CTR) of 1.25%, at an expenditure of $1,901. The campaign was expanded to include paid social media and ran from September 9 to November 13, 2020. Paid search resulted in 220,374 impressions with a 2.23% CTR. Paid social media resulted in 578,280 impressions and a CTR of 1.23%. Cost of the campaign was approximately $15,000. The campaign directed consumers to SCE’s Marketplace and to sce.com/rebates. | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 007 | With respect to the 1,904 personnel who monitored areas of electric lines and equipment in elevated fire risk conditions in 2020 (WMP Section 7.3.2.5), please provide the number who were employees of SCE at that time, as well as the number who performed monitoring as contractors. | The 1,904 figure in Section 7.3.2.5 is not number of personnel. As that section reads, SCE performed 1,904 pre-patrols and restoration patrols in 2020. While the unique number of individuals that performed these patrols is not easily separated from those that performed other kinds of patrols, SCE can confirm that all personnel used in 2020 to perform patrols referenced in Section 7.3.2.5 were SCE employees. These patrols typically entail one or two SCE employees, depending on resource types and availability. | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 008 | The 2021 WMP refers to a Salesforce-based application for tracking asset inspections and vegetation management.6 To what extent will this application, or the teams using it, use information from SCE’s “SPIDAMin” pole information database? | SCE is not currently planning to use pole loading data from SPIDAMin for the Salesforce-based application for tracking asset inspections and vegetation management. | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 009 | In what format(s) or database(s) has SCE tracked asset information for its Pole Loading Program between 2014 and 2020? (See WMP section 7.3.3.14) | The Pole Loading Program (PLP) retains data used for safety factor calculations, including necessary asset data attributes in SPIDAcalc, SCE’s pole loading software. The PLP also collects certain pole asset information via a Hana database. | 2021-02-22 | 2021-02-25
CalAdvocates-SCE-2021WMP-06 | 010 | a) What analysis or formula does SCE use to determine Access and Functional Needs (AFN) and Non-Residential Critical Infrastructure (NRCI) scores per circuit?7 b) Please provide a sample of 10 circuits with the Access and Functional Needs (AFN) and Non-Residential Critical Infrastructure (NRCI) scores for each. Select five circuits for which the majority of line-miles are located in HFTD areas and five circuits that do not traverse HFTD areas. | CONFIDENTIAL | 2021-02-22 | 2021-02-25
MGRA-SCE-004 | 001 | Provide all ignition data collected by SCE in the format provided in annual reports to the Safety Enforcement Division, for years 2015 to 2020. Confidential fields may be removed, for example if SCE considers location information confidential for transmission equipment it may omit necessary fields from transmission records. However, it should still provide location information for distribution data. | The attached file titled “MGRA-SCE-004-Question-001” contains all CPUC reportable ignition events reported between 2015 and 2019. Please note, the file contains 2020 data that is to be reported to the CPUC on April 1, 2021, and that data is still being finalized and may have some fields that are blank and still being populated. | 2021-02-22 | 2021-02-25
MGRA-SCE-004 | 002 | Has SCE omitted any wildfires from the list of ignitions for which it contests utility involvement, but which a public agency or SCE has publicly acknowledged is under investigation? If the answer to this question is “yes”, then list the name and ignition date of the fire(s) under investigation. | Yes. Below is a list of the fires, to the best of SCE’s knowledge, that were excluded from SCE’s annual ignition report because the fires were under active investigation at the time of reporting: VAN DYKE (2/6/2015), CABIN (8/14/2015), LINCOLN (8/16/2015), NICOLE (2/18/2016), EDISON (5/12/2016), ERSKINE (6/23/2016), MARINA (6/24/2016), BRAVO (5/12/2017), ELLIS (10/18/2017), THOMAS/KOENIGSTEIN (12/4/2017), MEYERS (12/5/2017), RYE (12/5/2017), LIBERTY (12/7/2017), HOLIDAY (7/6/2018), WOOLSEY (11/8/2018), PIRU (5/3/2019), STAR (7/28/2019), TENAJA (9/4/2019), SADDLE RIDGE (10/10/2019), OAK (10/28/2019), WALNUT (10/25/2019), EASY (10/30/2019), MUREAU (10/30/2019), MARIA (10/31/2019) Please note, for years 2018 and prior, this was a manual search, and SCE made reasonable efforts to include all that it knew were not contained in the annual filing within the limits of the 3-day response period. Additionally, in 2019, four smaller events (10/5/2019, 10/21/2019, 11/27/2019, 11/28/2019) that involved civil litigation were excluded. SCE is not producing events that may be excluded from its 2020 report, which will be submitted on April 1, 2021, because the filing is not finalized and is still under review. | 2021-02-22 | 2021-02-25
MGRA-SCE-004 | 003 | Provide all wires down data from 2015 to 2020, including all non-confidential fields maintained in the SCE database. Position information should be in terms of latitude/longitude. If latitude/longitude is not available, then ID of nearest structure should be provided. If ID of nearest structure is not available provide circuit ID and feeder number. Additionally, data provided should include date/time of wire-down, cause of wire down, supplemental cause information on wire down, weather information, major event day information, event id, equipment involved, fault type, ignition involved, if ignition involved, cross reference to ignition ID in MGRA-16, if vegetation caused, diagnosis of tree failure. | The attached spreadsheet titled “MGRA-SCE-004-Question-003.xlsx” contains all wire downs between 2015 to 2020. The data set contains all non-confidential fields in the database. The database does not track weather, tree health or whether an ignition occurred. However, SCE attempted to match vegetation and ignition records to the outage data by using circuit and date of the event although this may not always be correct. For example, there could be multiple events on the same day. Furthermore, given the limited time to respond to this data request, SCE is unable to provide weather data for the events listed in the Excel file. | 2021-02-22 | 2021-02-25
MGRA-SCE-004 | 004 | Provide all outage data from 2015 to 2020, including all non-confidential fields maintained in the SCE database. Position information should be in terms of latitude/longitude. If latitude/longitude is not available, then ID of nearest structure should be provided. If ID of nearest structure is not available provide circuit ID and feeder number. Additionally, data provided should include date/time of wire-down, cause of outage, supplemental cause information on outage, weather information, major event day information, event id, equipment involved, fault type, ignition involved, if ignition involved, cross reference to ignition ID in MGRA-16, if vegetation caused, diagnosis of tree failure. | The attached spreadsheet entitled “MGRA-SCE-004-Question-004.xlsx” contains all outage data that was used to create SCE’s WMP fault tables between 2015 to 2020. SCE has excluded all restoration steps, and outages that were not faults (i.e., crew caused). The database does not track weather, tree health or if an ignition occurred. However, SCE attempted to match vegetation and ignition records to the outage data. SCE attempted to match these records by using circuit and date of the event. However, this may not be always correct. For example, there could be multiple events on the same day. Furthermore, within the shortened response time, SCE is unable to provide weather data for the events listed in the Excel file. | 2021-02-22 | 2021-02-25
TURN-SCE-001 | 001. c Amended | Re SCE Excel data attachment, Table 2, subpart 7 (“Number of ignitions”) and sub-parts: a. Please confirm that SCE has included all CPUC reportable ignitions in this data set. b. If SCE has not included all ignitions, please re-produce all rows of #7 (7a- 7d) in Excel to include all reportable ignitions in each year for each category. c. Please provide the CPUC reportable ignition database, including all columns and rows, which part (b) is based on. c. Amended: Part (c) asks for the CPUC reportable ignition database, including all rows and columns, which TURN understands is more than SCE provided in its WMP filings. Can SCE please provide this in Excel? | The attached file titled “2015-2020 CPUC Reportable Igintions.xlsx,” contains the requested information. | 2021-02-22 | 2021-02-25
TURN-SCE-003 | 001 | Please provide in Excel the number of utility distribution wood poles segregated by size class (ANSI O5.1 – 2017) separately for HFTD and non-HFTD areas, as they were at the end of 2018, 2019 and 2020. Please also provide the number of non-wood poles. Please use the following spreadsheet design, with separate sheets for each year. Please contact TURN if a different format would be more appropriate. | The attached file Response TURN-SCE-003 -Q01.xlsx, contains the requested information. To answer this question, SCE queried SAP, its system of record. Please note that the data is a snapshot in time and as with all recorded data it is subject to update/refinement. | 2021-02-24 | 2021-03-02
TURN-SCE-003 | 002 | Please provide the total number of distribution poles a) removed and b) installed in Tiers 2 and 3, similarly segregated by size class. | The file entitled Response TURN-SCE-003-Q02.xlsx contains the requested information. Please note that the data is a snapshot in time and as with all recorded data it is subject to update/refinement. | 2021-02-24 | 2021-03-02
TURN-SCE-003 | 003 | Please provide the number of overhead distribution circuit miles located in Tiers 1, 2 and 3 and non-HFTD areas, at the end of each year 2018, 2019 and 2020. | The below table contains the overhead distribution circuit miles by year and fire designation. | 2021-02-24 | 2021-03-02
MGRA-SCE-005 | 001 | The response to Data Request MGRA-3 (GIS PSPS damage data) was incomplete: • The data lacks any “cause” information. • SCE’s PSPS reports list one instance of equipment damage in its November 24th Report, 9 instances of equipment damage in its November 29th report, and 8 instances of equipment damage in its December 4th report. This is a total of 18 instances of damage. Only 10 are listed in the GIS data provided to MGRA. Repeating language from MGRA-3: “Please provide the most recent available geodatabase comprised of the non-confidential portion of the GIS data uploaded to the WSD website containing PSPS Event records including specifically all perimeter, timing, and damage data that is reported to WSD and to the Safety Enforcement Division as part of PSPS event reporting. Damage records should include at the least location, type of damage, any photos, and date and time of report. Customer meter records may be omitted from the data response.” (emphasis added) By “type of damage” MGRA is referring to the cause of the damage recorded by SCE. Provide data for all 18 events referred to in SCE’s post-incident PSPS reports. | The tables below provide the requested information. As MGRA states, 18 instances of damage were listed in the PSPS post-event reports, but only ten were in the data provided in SCE’s response. The 18 instances referenced in the question do not include incidents for the 10.23.2020 and 12.16.2020 Post Event Reports, and the Q4 2020 Quarterly Data Report (QDR) did take all of them into account. The corrections are summarized below with details in the tables. Post Event Report:  Reported: 29 structures (reported in 21 line entries)  Reported incorrectly: 12 structures (subtract) – details shown in Table 1 below  Missed reporting: 1 structure (added) – detail shown in table 2 below  Accurate count: 18 structures Q4 2020 Quarterly Data Report:  Reported: 10 structures  Reported incorrectly: 0 structures (subtract) MGRA-SCE-005: 001 Page 2 of 3  Missed reporting: 8 structures (added) – details shown in table 2 below  Accurate number: 18 structures The following items were included Table | 2021-02-25 | 2021-03-02
CalAdvocates-SCE-2021WMP-07 | 001 | The table in attached Excel file “CalAdvocates-SCE-2021WMP-07_Attachment A” lists distribution circuits on your system with high wildfire risk scores. In an Excel table, please provide the following data on the wildfire mitigation work you plan to complete in 2021 on each of the identified circuits: a) Miles of covered conductor to be installed b) Miles of underground conductor to be installed c) Number of expulsion fuses to be replaced with CAL FIRE exempt fuses d) Total number of non-exempt expulsion fuses on the circuit, as of January 1, 2021 e) Number of circuit breaker relays to be installed f) Number of Canyon patrols g) Number of At-Risk Circuit Patrols h) Number of Operation Santa Ana patrols | a) Please see the attached excel file. The included values represent all work that is currently planned for construction on the mentioned circuits. Scope and timing of planned work on these circuits may change as ongoing reviews are conducted against these circuits. b) Please see the attached excel file. The included values represent all work that is currently planned for construction on the mentioned circuits. Scope and timing of planned work on these circuits may change as ongoing reviews are conducted against these circuits. c) Based on available data, SCE is providing quantities for fuse replacements related to wildfire initiative SH-4, SCE’s branch line protection strategy included in our 2021 WMP Update. SCE also replaces both expulsion and non-expulsion fuses outside of SH-4 which are not included in this response as these additional fuse replacements do not have specific targets in the Wildfire Mitigation Plan and are generally preformed as part of bundling work for efficiency purposes. d) Based on available data, SCE is providing quantities of non-exempt expulsion fuses identified as branch line fuses, in alignment with efforts for SCEs branch line protection strategy (SH-4). The SH-4 efforts are limited to branch line fuse applications which serve circuitry which extends into SCEs HFRA, rather than the entire circuit. Additional non-exempt fusing may exist for other fusing CalAdvocates-SCE-2021WMP-07: 001 Page 2 of 2 applications on the circuit such as equipment fusing, and is not included in this response as this is out of scope for SH-4. e) Please see the attached Excel file. The included values represent all work that is currently planned for construction on the mentioned circuits. Scope and timing of planned work on these circuits may change as ongoing reviews are conducted against these circuits. f) Canyon Patrols – Are performed annually on approximately 120 areas to verify circuits, or portions thereof, are free from vegetation encroachment into the minimum vegetation clearance distance and level 1 hazard tree assessments. The canyons included for inspection are typically selected based on risk factors such as high winds, terrain, ingress/egress issues, type of electrical facilities, or known tree characteristics. SCE plans to continue with the historic plan in 2021 and the following two Excel files are provided which indicate (1) the Canyon Patrols, and (2) Canyon Patrols that are included in Attachment A. • Excel File “CalAdvocates-SCE-2021WMP-07_canyon_patrol.xlsx” provides a list of Canyon Patrols planned for 2021 • Excel File “CalAdvocates-SCE-2021WMP-07_Attachment A.xlsx” indicates which Canyon Patrols are scheduled that are included in Attachment A g) At-Risk Circuit Patrols – When referring to SCE’s At-Risk circuits, this term is implied as a cumulative term to capture Canyon Patrols, DRI and HTMP. Refer to (f) for list of Canyon Patrols and the following Excel file for list of HTMP and DRI circuits planned for inspection in 2021. • Excel File “2021_HTMP DRI Circuit List.xlsx” h) Operations Santa Ana Patrols – Will continue in 2021 with a patrol focus on non-exempt PRC 4292 equipment and limited PRC 4293 inspections to identify potential encroachments in State Responsibility Areas. The schedule and locations of these patrols is informed by the local Fire Agency Lead and the respective SCE Lead to provide reasonable assurance of compliance to ensure the pole brushing activities meets agency expectations. The actual scope and schedule is determined just prior to the Operation Santa Ana activity, and therefore, a list is not currently available. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-07 | 002 | Regarding covered conductor installation on distribution circuits, please provide your workplan that describes where and when you will undertake covered conductor installation projects in 2021. | In the attached file is a summary of anticipated construction start and end dates for covered conductor projects forecasted to be completed in 2021 and approximate location information (i.e., SCE region, SCE district, and city). This information should be considered a point-in-time estimate and highly dependent on operational conditions such as site accessibility, weather conditions, customer outage restrictions, and agency constraints. Unexpected delays in the design, permitting, and construction processes may result in projects being deferred. In anticipation of these constraints, SCE has scoped a larger volume of work (over 1,880 miles is contained in this project list) to ensure an adequate number of projects are made available. Furthermore, the scope and timing of planned work on these circuits may change as ongoing reviews are conducted against these circuits. | 2021-02-26 | 2021-03-04
CalAdvocates-SCE-2021WMP-07 | 003 | In your response to CalAdvocates-SCE-2021WMP-02, Question 1, you stated that SCE does not have a climbing inspection program and that climbing of transmission towers may occur to perform maintenance or in response to an emergent condition. a) Has SCE performed climbing inspections on transmission structures over the last 5 years for reasons other than maintenance or dealing with emergent conditions? b) If the response to 3(a) above is “yes”, how many corrective tags were generated as a result of those inspections? c) If the response to 3(a) above is “yes”, explain why SCE discontinued climbing inspections on transmission structures for these other reasons besides maintenance or dealing with emergent conditions. d) If the response to 3(a) above is “no”, has SCE considered conducting such climbing inspections and if so, explain why SCE chose not to conduct such climbing inspections of transmission structures. | a) No, SCE does not have, and has not had in the last 5 years, a climbing inspection program. There are times when personnel performing an inspection may choose to climb a structure to get a better view of a suspected issue, but this is done on an ad-hoc basis and is not formally documented as a climbing inspection. b) N/A c) N/A d) In 2019, as SCE was developing its enhanced high fire overhead inspection program, a number of methods were considered, including programmatic climbing inspections. SCE decided against pursuing this type of program as it was deemed less efficient, and no more effective, than its current method of pairing ground-based visual inspections with aerial inspections. Climbing inspections would require significantly more time at a structure and more personnel present to ensure appropriate safety protocols are in place. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-07 | 004 | Regarding your discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations (7.3.4.9, programs IN-1.1 and IN-5): a) What are the “Alternate Units” provided in Table 12 for these programs? b) Within these programs, on what number of alternative units and line-miles did SCE perform aerial inspections? c) Within those aerial inspections discussed in 4(b), what percentage of inspections were carried out using helicopters? d) Within those aerial inspections discussed in 4(b), what percentage of inspections were carried out using unmanned drones? e) What amount of capital expenditures (CAPEX) did SCE incur on the aerial inspections specified in 4(c)? f) What amount of operating expenses (OPEX) did SCE incur on the aerial inspections specified in 4(c)? g) What amount of capital expenditures (CAPEX) did SCE incur on the aerial inspections specified in 4(d)? h) What amount of operating expenses (OPEX) did SCE incur on the aerial inspections specified in 4(d)? | a. The alternate units listed in Table 12 for IN-1.1 is structures for inspections, and repair notifications for remediations. b. As noted in Table 12, in 2020, SCE performed 168k aerial inspections. c. Of the inspections performed in 2020, 80% were conducted using helicopters. d. Of the inspections performed in 2020, 20% were conducted using drones. e. SCE did not incur any capital expenditures to perform these aerial inspections. Further, SCE does not track remediation costs as to which type of aerial inspection generated the need for the repair work. f. SCE incurred $14.3M in operating expenses to perform image captures by helicopter. Additionally, SCE incurred $23M in total for data capture of both drone and helicopter images. SCE does not track remediation costs as to which type of aerial inspection generated the need for the repair work. g. SCE did not incur any capital expenditures to perform these aerial inspections. Further, SCE CalAdvocates-SCE-2021WMP-07: 004 Page 2 of 2 does not track remediation costs as to which type of aerial inspection generated the need for the repair work. h. SCE incurred $3.9M in operating expense to perform image captures by drone. Additionally, SCE incurred $23M in total for data capture of both drone and helicopter images. SCE does not track remediation costs as to which type of aerial inspection generated the need for the repair work. Response from Generation IN-5 a. The alternate units listed in Table 12 for IN-5 is structures for inspections and repair notifications for remediations. b. 0 aerial inspections - Generation does not utilize aerial inspections for IN-5. c. 0% - Not applicable d. 0% - Not applicable e. 0 capital – Generation does not utilize aerial inspections for IN-5 f. 0 operating expenses - Generation does not utilize aerial inspections for IN-5 g. 0 capital – Generation does not utilize aerial inspections for IN-5 h. 0 operating expenses - Generation does not utilize aerial inspections for IN-5 | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 001 | What is the timeline for integrating SCE's new Machine Learning model into its PSPS decision-making? i. How will SCE validate the model? ii. What inputs does the model use? | SCE, through its vendor, Atmospheric Data Solutions, is expected to have machine learning models completed for 50 site-specific station locations by May 1, 2021. Integration of this model output data into the PSPS decision making is anticipated to occur in Q4 2021. SCE will validate every model (which is specific for each weather station location) using station observations. Each model will be validated using station observation data from multiple weather events which were not included for the development of the model. Ultimately, final inputs are determined at the time of model development, but SCE will typically use friction velocity, near surface wind speed, and wind speed from multiple levels above the surface. Data from the outer most and the inner most model domains (regions) are used to provide geographical and meteorological context. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 002 | What specific actions or initiatives outlined in SCE’s 2021 WMP will improve PSPS notifications in 2021 to avoid false positive communications? | False positives reflect the variance between SCE’s long-range weather forecasting at the circuit level, which is the basis of initial (e.g., 72-hour, 48-hour and 24-hour) customer notifications, and de-energization decisions, which are based on real-time conditions at the circuit-segment level. Targeted real-time decision-making at the circuit-segment level allows SCE to de-energize as few customers as possible, based on actual weather conditions and as a last resort. SCE will continue to reduce PSPS impacts to individual customers during events by using real-time weather information rather than forecasting to make de-energization decisions, and by de-energizing only necessary segments of circuits, rather than entire circuits, even when all customers on a circuit may have initially been in scope for potential de-energization and received notifications to that effect. However, improved in-house forecasting capabilities1 should reduce the number of customers in scope and will therefore reduce the variance between the customers who are notified of potential de-energization and the customers who are actually de-energized due to onset of increased fire danger conditions. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 003 | How has SCE customized its weather research and forecasting model since its 2020 WMP? a. Currently, what fuel moisture values are used, and at what granularity, in SCE’s weather research and forecasting model? How is this data collected? | SCE through its vendor, Atmospheric Data Solutions, implemented a multi-physics North American Model ensemble. This was a result of an extensive validation effort which consisted of comparing ensemble output against SCE weather station observations for the following meteorological variables: wind speed, wind gusts, temperature, and dew point for 7 weather events. The fuel moisture variables that SCE uses are Live Fuel Moisture, Dead Fuel Moisture (1-hour, 10-hour, 100-hour, and 1000-hour timelags), and green-up. Green-up is a measure of greenness that is present in the annual grasses which develop during the spring months. SCE’s weather modeling is performed at a 2 km resolution which means there is a data point every 1.6 miles across the service territory. SCE’s in-house weather modeling is produced twice a day with outputs in the form of static graphic images and csv files. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 004 | SCE considers any Fire Potential Index (FPI) score above 12 “high risk”. In its PSPS postevent reports in 2020, SCE identified many circuits as “elevated” risk with an FPI score of 12. a) Please explain the distinction between “elevated” risk and “high” risk. b) How does the distinction between “elevated” and “high” risk affect SCE’s PSPS decision-making? | SCE’s Fire Potential Index (FPI) is broken into three categories: Normal, Elevated, and Extreme. The FPI breakpoints for these categories are as follows: Normal – FPI < 12 Elevated – FPI >= 12 and FPI < 15 Extreme – FPI >= 15 SCE will initiate PSPS if the FPI is 12 or greater which is considered “high risk” for wildfires even though FPI values between 12 and 15 are in the “Elevated” category. If PSPS wind speed and FPI criteria are met, SCE will begin to notify its customers about potential proactive de-energizations, so in this case there is no distinction between “elevated” risk and “high” risk. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 005 | SCE states that it is making circuit threshold adjustments. How is SCE making these adjustments? | The circuit threshold adjustments referenced in this question are driven by installation of covered conductor on SCE’s HFRA circuits. Once a circuit is fully installed with covered conductor and this condition is verified in the field, SCE adjusts its PSPS algorithm to reflect the current methodology of using the National Weather Service’s High Wind Warning. This revises the threshold to 40mph sustained winds and 58mph wind gusts for that particular circuit or isolatable circuit segment. Isolatable circuit segments that are completely installed with covered conductor will still have their activation and notification thresholds set at the lower of their 99th percentile wind speed and the National Weather Service’s Wind Advisor if other HFRA portions of the circuit remain bare. However, de-energization triggers for that isolatable segment will be set using the High Wind Warning values. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 006 | SCE states that outstanding maintenance items are a criterion for PSPS. Does SCE prioritize these maintenance items to mitigate the scope of PSPS events? If so, how? In your answer also please also specify the age threshold of these maintenance items to be prioritized, if existing. | SCE uses outstanding maintenance items as an input for determining PSPS de-energization triggers if those maintenance items are likely to be exacerbated by wind conditions SCE prioritizes remediation of maintenance items in accordance with the timelines defined under CPUC General Order 95. SCE also prioritizes remediation of maintenance items that are used to inform PSPS de-energization triggers when possible. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 007 | What impact does SCE expect its Next-generation weather forecasting system will have on future FPI calculations? | SCE will be developing and implementing its Next Generation Weather Modeling System in Q3 and Q4 of 2021. This will include a more robust ensemble forecast output at a 1 km resolution. Currently, SCE is modeling the atmosphere at a 2 km resolution. The combination of increasing the resolution from 2 km to 1 km, and increasing the number of ensemble members, is expected to provide more accurate forecasts of wind speeds and other variables necessary to calculate FPI. Since major terrain features will be better resolved by the model at a 1 km resolution, SCE expects model output to be improved, particularly with regards to wind speeds. These improvements in model output will be directly reflected in FPI accuracy at the circuit level. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 008 | In the WMP workshops on February 22-23, SCE stated that it is developing a PSPS risk model to quantify the risks of PSPS events. a) What data sources is SCE using to develop this risk model? b) What safety risks to the public will this model include? c) Will this model include economic costs to customers from PSPS events? If so, please describe which costs will be addressed. | a) SCE’s PSPS risk model data sources include the following: 10-year historical wind/gust and FPI data; Wind/gust thresholds for HFRA circuits based on the current PSPS operation protocol; Customer count at circuit level; AFN (Access and Function Needs) and NRCI (Non-Residential Critical Infrastructure) multiplier at circuit level. b) Given the limited information directly linking safety consequences to a PSPS event, SCE used the 2003 Northeast Blackout event as a data point to determine safety impacts from an outage. Other data points include the 2011 Southwest blackout and the 2019 PSPS outages in SCE’s service area. c) Yes. The current financial impact to customers is modeled as $250/Customer/Event. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 009 | How do your criteria for determining whether to implement a PSPS event differ for circuitsegments where covered conductor has been installed, compared to circuit-segments with bare overhead conductor? | As discussed in question 5, SCE uses the National Weather Service’s High Wind Warning of 40 mph sustained winds and 58 mph wind gusts as the threshold for fully covered circuits and isolatable circuit segments. Distribution circuits with bare overhead conductor use the lower of their 99th percentile historical wind speeds and the National Weather Service’s Wind Advisory of 31 mph sustained and 46 mph wind gusts. | 2021-02-26 | 2021-03-03
CalAdvocates-SCE-2021WMP-08 | 010 | a) Are you aware of any plans to change your criteria for implementing PSPS events on covered conductor segments? b) If the answer to part (a) is yes, to your knowledge, when will SCE implement its new or modified criteria? c) What evidence or considerations are you using to develop new criteria or modify existing criteria? | Please see response to question 5 for an explanation of SCE’s plans to change its criteria for implementing PSPS events on circuits with covered conductor. | 2021-02-26 | 2021-03-03
WSD-SCE-002 | 001 | Explain your company’s grid infrastructure rebuild standards (e.g., under-grounding, covered conductor, etc.) utilized for post-fire repairs and replacements. | It is important for SCE to rebuild damaged infrastructure to the current SCE standards in an expedient manner to quickly restore power for the impacted customers after a fire. To help ensure quick restoration, SCE typically uses the same circuit routing and structure location, and keeps undamaged equipment. In addition, SCE typically replaces in a like-for-like infrastructure configuration, e.g., overhead facilities remain overhead, and underground facilities would remain underground. The process starts with a thorough infrastructure assessment. This process helps SCE to identify damaged equipment and develop a comprehensive restoration plan, including design, equipment inventory and resources ramp-up, etc. SCE’s post-fire rebuild strategy follows the design standards for HFRA as described in SCE’s 2021 WMP Update Grid Hardening sections that includes covered conductor, fire-resistant pole (composite for intumescent wrap wood), composite cross arms, wildlife protection covers, CAL FIRE exempt materials such as spark prevention lightning arrestors, current limiting fuses, connectors, wildlife protection covers, switches, and transformers. | 2021-03-01 | 2021-03-04
WSD-SCE-002 | 2 a. and c. | In order to demonstrate adequacy of size of service restoration workforce (requirement 8386(c)(15)) provide the following: a. Describe your current service restoration processes (i.e., damage assessments, repairs, switching activities, etc.) and tools (boots on the ground, drones, helicopters, etc.). c. How many mutual aid agreements does the utility have in place? Explain the type and number of personnel classifications involved in each agreement (or the total number for all agreements). | a) SCE believes the question is intended to reference requirement 8386(c)(13). SCE may have more than one Storm incident concurrently and may employ different damage assessment and restoration strategies based on the size, scope, and intensity of each incident. In smaller, more isolated incidents, SCE typically employs the standard order-based strategy that it uses under routine outage circumstances. As described below, this strategy is not effective in larger incidents where there is an overwhelming volume of orders. When incidents are larger, SCE moves to an area-based strategy where repair priorities are assigned by areas and circuits. This is a tactical decision made during the planning process for a given operational period and documented in the Incident Action Plan. The two strategy types, order-and area-based can be used together within an event as needed. RESTORATION PRIORITIZATION Due to the wide range and nature of incidents, SCE has identified guidelines to restore both the most critical and the largest numbers of customers as quickly as possible while prioritizing public health and safety. With safety of the public and employees as our priority, restoration efforts need to be done in the most efficient manner possible while also maintaining critical infrastructure. Restoration priority strategy will be based on the following: • If there is a total or partial system shutdown and subsequent restoration, SCE’s priority is to deliver off-site power for bulk power generation start-up. During the process of routing power, some customer load may be restored while energizing bulk power transformers for the coordination of protective relaying equipment, for voltage control, and while picking up station light and power • Startup power for bulk power generation • Switching Centers station light and power (if not carried by the emergency generator) • Offsite power to Diablo and Palo Verde Nuclear Generating Stations if required • Bulk Power Substations station light and power (if not carried by the emergency generator) • Customer load If the total system is not shut down: • Protect public safety and ensure that utilities and public agencies have electricity • Repair any facilities that have sustained damage • Repair transmission lines (66 to 500 kV) • Ensure substations and circuits are energized • Repair distribution lines (4 to 66 kV) to restore/maintain service to large numbers of customers • Repair tap lines to restore service to smaller numbers of customers • Repair individual customer problems Additional information can be found in SCE’s Storm Response Plan, attached, developed in accordance with GO 166. Please also see SCE’s Response to Q.2 part b. c) SCE has 1,690 field personnel who are able to conduct electrical restoration. In addition to the nearly 1,700 field employees, SCE can call upon thousands of line workers across the country to support restoration of electric service. In 2018 after hurricane Maria devastated the electrical infrastructure of Puerto Rico SCE and approximately 60 other electric utilities sent 3000 line workers to there to restore electric services. Currently, the Mutual Assistance Agreements (MAA) that exist are: (1) California Utilities Emergency Association (CUEA), among California utilities; (2) Western Regional Mutual Assistance (WRMAA), a regional agreement; (3) Edison Electric Institute (EEI), a national mutual assistance program. When it is believed that SCE will not be able to provide restoration service to its customers within a reasonable time frame with its existing work force, SCE may call upon the member utilities that are a party to the MAAs listed above and request mutual assistance. These agreements do not limit types of personnel classifications that can be requested, nor do they limit or specify types of equipment that may be requested. | 2021-03-01 | 2021-03-04
WSD-SCE-002 | 2 b. and d. | In order to demonstrate adequacy of size of service restoration workforce (requirement 8386(c)(15)) provide the following: b. Report the type and number of each personnel classification currently employed by [insert utility] that are involved in service restoration activities, including an explanation of what roles and responsibilities they have. d. How many contractors are in place for service restoration? Explain the type and number of personnel classifications retained as contractors | SCE details its service restoration activities in Section 7.3.9.1 of its 2021 WMP Update, as well as in its Storm Response Plan filed pursuant to General Order 166. As discussed in these materials, SCE maintains a large, highly skilled field workforce (both employees and contractors) to provide effective emergency response and restoration of service during and after a major event. In addition, SCE’s existing mutual assistance agreements, as discussed in more detail in response to question 2(c), can be activated in situations where the response exceeds the capacity of SCE’s crews and emergency contracting capabilities. SCE currently employs nearly 1,700 transmission and distribution field workers in the job classifications identified below (as of February 2021). During and after an event requiring service restoration, SCE will draw upon these field crews to restore service quickly and safely. The specific number of resources that are used to restore service after an event depends on the size and scope of the event and associated restoration required. These positions consist of: Table SCE supplements its employee field workforce by using external contractors. These contractor resources help to maintain SCE’s electric system and provide electric service to our customers. This includes restoring power to customers after an event. Over the past year, SCE has had on average 227 distribution four-man equivalent contractor crews and 13 transmission 6-man equivalent contractor crews. The worker titles and functions of workers within these contractor crews are similar to those for SCE employee crews, however, each contractor determines the composition of specific personnel classifications necessary to complete the requested work. In addition, SCE may also solicit new contractor resources as necessary to meet demands. As discussed in Section 7.9.3 of the 2021 WMP Update, SCE maintains detailed plans and procedures to anticipate and respond to emergency events. This includes a robust Incident Management Team (IMT) structure that can be organized to respond to events of different sizes. The IMT is primarily staffed by trained SCE employees who perform various monitoring, communications, logistical, and other functions to support restoration work, when such work arises. Outside of IMT events, these employees fulfill their normal job functions. For reference, SCE has trained over 500 employees as qualified IMT members. | 2021-03-01 | 2021-03-04
WSD-SCE-002 | 003 | Enter the total circuit miles for each category in the following table. HFTD = High Fire Threat District, Tx = Transmission Lines, Dx = Distribution Lines, OH = Overhead, UG = Underground | Please find the requested data in the table below. | 2021-03-01 | 2021-03-03
WSD-SCE-002 | 004 | From the inception of your Public Safety Power Shutoffs (PSPS) program, provide the number of customer hours “on alert” for a PSPS, broken out by calendar year, calculated as the amount of subsections (a) multiplied by (b) below: a. time between an initial notification of a potential PSPS and a notification of cancellation of PSPS b. the amount of customers who received both notifications | Please see the table below that provides the customer counts, total hours, and average customer hours by year for the time between an initial notification of a potential PSPS and an all-clear notification (i.e., notification of cancellation of a PSPS) excluding those customers that were de-energized. In 2019, SCE, where possible, typically sent notifications to impacted customers for circuits in scope for potential de-energization 48 hours in advance. In 2020, SCE began notifying, where possible, critical infrastructure customers (e.g., first responders, telecommunication providers, water providers, etc.) 72 hours in advance and non-critical infrastructure customers 48 hours in advance. The data used is from SCE’s Emergency Outage Notification System (EONS) that was previously extracted by event. SCE compiled the data by event and customer using the date/time stamp from initial notification and the date/time stamp from SCE’s all-clear notification that removed customers from the scope of a potential PSPS de-energization. In order to compile the information in the table above, SCE notes that this information contains duplicate customer counts if a customer was impacted by more than one PSPS event. Average Customer Hours by Year were calculated by division of Total Number of Hours by Customer Count. All-clear notification applies to those on notice but never de-energized. Please also note that the dataset is large (millions of records) and not available via export to Excel. | 2021-03-01 | 2021-03-11
MGRA-SCE-006 | 001 | What are the variables from the historical weather data that are used by POI? | The POI model uses solar radiation, humidity, precipitation, temperature, dew point temperature, wet bulb temperature, atmospheric pressure, and wind speed, direction, and frequency of oscillation, from SCE weather stations and WRF climatology model data generated by Atmospheric Data Solutions (ADS). | 2021-03-03 | 2021-03-08
MGRA-SCE-006 | 002 | What kind of wind data is utilized as an input to the machine learning model? Gust or average wind speeds? And are averages used (if so over what time period), peak values (if so over what time period), or value at point of failure using Historical Failure Data? | Ten years (2009-2019) of hourly wind data including the peak (gusts), average, and standard deviation of observed wind distribution are used in the models. | 2021-03-03 | 2021-03-08
MGRA-SCE-006 | 003 | Describe the algorithm(s) used by the POI model. “Machine learning” is not sufficient detail. | The POI model uses a form of ensemble model called a “Random Forest Classifier.” Ensemble models use a group or “ensemble” of decision trees to make classifications. The Random Forest Classifier takes subsets of random samples of the training data set and fits a decision tree on the independent variables that best discriminates between the classes of interest. The order with which the algorithm chooses variables to build out the decision trees is also randomized. Future data is classified based on the consensus of “votes” of the ensemble of decision trees. Classifications in the context of POI models determine whether an asset experienced a failure given its physical features and the environmental and electrical stresses, and other data that the asset may experience. The Random Forest Classifier, therefore, creates a congress of logic trees that determine the likelihood of an asset failure. | 2021-03-03 | 2021-03-08
MGRA-SCE-006 | 004 | When making predictions for an ignition to be used as input for consequence modeling, what assumptions are input to the POI model regarding weather conditions? Is the probability of ignition averaged over all historic weather conditions? Or is POI based on a specific weather scenario also used for Technosylva fire spread modeling? | Hourly weather features are aggregated to their mean, max, and standard deviation over 10 years to capture the cumulative, average, and extreme impacts from weather conditions on equipment failures that are likely to cause ignitions. Therefore, the POI model was not based on the specific weather scenario used for Technosylva fire spread modeling but was built using all outages capable of generating a spark regardless of the weather condition at the time of the outage. | 2021-03-03 | 2021-03-08
MGRA-SCE-006 | 005 | During the February 22nd technical workshop, Joe Goizueta of SCE commented that SCE had not observed correlation between wind speeds and outage rates. Please confirm whether this is an accurate statement and if so provide data and analysis supporting it. | Mr. Goizueta’s statement was referring to circuit level correlations and was based on a limited sample of data and Mr. Goizueta’s expert judgment. SCE has observed correlations for 10% of circuits for which there was available data. For most circuits, SCE does not have enough-wind driven outage data at the circuit level to make determinations about correlations between wind speeds and outage rates. | 2021-03-03 | 2021-03-08
MGRA-SCE-006 | 006 | SDG&E observes the following probabilities for ignitions arising from outages: SCE’s POI model uses only outages, not ignitions, as input. What assumptions does it make about probability of ignition from any given outage? | SCE’s POI model was developed in two steps. The first step is to output the probability of spark-causing outages at sub driver level (e.g., CFO, EFF). Not all sparks-causing outages lead to ignitions, as ignitions may depend on the presence of other factors such as weather and fuels. The second step is to calibrate the output to POI by calibrating against historical fires. The calibration is performed at the sub driver level so that the results reflect the outage to ignition potential. This calibration gives us greater granularity than applying a probability across the entire area. For example, we can estimate total ignitions across a territory as well as estimate ignitions from an equipment failure versus a vegetation contact at a segment or circuit level. | 2021-03-03 | 2021-03-08
MGRA-SCE-006 | 007 | In its response to Cal Advocates Data Request CalAdvocates-SCE-2021WMP-01, SCE states that “SCE plans to assess the feasibility of replacing the current methodology for setting PSPS thresholds and triggers with a dynamic, machine-learning model that derives circuit thresholds and triggers. SCE began the development of this model in 2020 and will perform rigorous analysis and validation in 2021.” How does this machine learning model differ from POI? What algorithms will it use and what specific data will it analyze (in particular weather data)? | The POI model is the same as the machine learning model which creates probability of ignitions at the FLOC level. Results of the POI model are used as inputs to the dynamic PSPS threshold and trigger model (PSPS model). The PSPS model uses historical wind speeds and wind-driven outages data to enhance the POI model predictions such that the POI changes as the impacts from wind/gust speeds changes. Unlike the POI model, the PSPS model uses an algorithm that results in outputs that are dynamic, changing with wind/gust speeds. The PSPS model also leverages FPI data and engineering design capacity to set the risk-informed PSPS threshold and trigger for each HFRA circuit. In addition to POI model results, data used in the dynamic PSPS model include ADS (Atmosphere Data Solutions) hourly historical wind/gust speeds at a 2 km horizontal resolution, SCE historical outages, historical FPI, and SCE circuit connectivity. Currently the feasibility of this method is still being evaluated. SCE plans to make enhancements to the PSPS model and perform rigorous analysis and validation in 2021. | 2021-03-03 | 2021-03-09
MGRA-SCE-006 | 008 | Please provide a table of all trees removed in 2018-2020, including columns for year, species type, species (if available), distance from SCE equipment (if available), and reason for removal (if available). | SCE removes trees under three vegetation management programs: (1) Routine Compliance; (2) Hazard Tree; and (3) Dead & Dying Tree removal (formerly DRI). Routine compliance – work is performed throughout SCE’s service territory. SCE is providing the total number of trees removed for 2018, 2019 and 2020. Additionally, SCE is providing trees removed in HFRA and non-HFRA for 2019 and 2020. However, due to work management systems issues encountered in 2018 and 2019, actual tree information is not readily available. For 2020 routine compliance/line clearing work, SCE is providing quantities and species information. Distance from SCE equipment and reason for removal is not available. • See attached Excel File: Q8_Routine_Tree_Removals_2020.xlsx Hazard Tree – hazard tree commenced in 2019 and therefore, no data is provided for 2018. In 2019, 5,273 Hazard trees were removed, and in 2020, 10,887 Hazard trees were removed. Hazard tree work is only performed in HFRA. SCE is providing quantities and species information. Trees were removed because they were deemed a hazard based on the score produced from the tree risk calculator and/or ISA assessors professional judgment. Distance from SCE equipment is not available. • See attached Excel File: Q8_HTMP_Trees_Removed.xlsx Dead and Dying Tree removals – this program was formerly SCE’s Drought Relief Initiative (DRI) program. SCE is providing quantities, species and reason for removal when noted (Fulcrum data only). Distance from SCE equipment is not available. In 2018 and 2019, SCE used a paper tracking system and therefore, only quantity removed is available for those years. In 2020, SCE used two field tools for work management: (1) Fulcrum, and (2) Arbora. Of the 6,364 trees removed, 6,290 are documented in Fulcrum, and 74 are documented in Arbora. • See attached Excel File: Q8_DRI_Trees_Removed_Fulcrum (6290).xlsx • See attached Excel File: Q8_DRI_Trees_Removed_Arbora(74).xlsx Table 1 – Tree Removals 2018-2020 | 2021-03-03 | 2021-03-09
MGRA-SCE-006 | 009 | Please provide details of the consequence modeling portion of the WRRM component that calculates the risk of PSPS de-energization based on the probability of de-energization and consequence of those de-energizations (safety, reliability and financial) at the circuit level. | Please refer to SCE’s 2021 WMP Update Table SCE 4-6 pages 59-61 for the detailed current consequence modeling for the risk of PSPS de-energization. The WMP states the PSPS de-energization consequence is broken up into three components which are: safety, reliability and financial. • Reliability is based on the product of the number of customers downstream that are impacted by a de-energization on a circuit and the duration, which is based on a historic back casting of 10 years of data. • Financial impact is estimated as $250 per customer per event informed by internal claims data. • Safety is the number of customers impacted multiplied by a safety consequence variable. The safety consequence variable was calculated using the 2003 Northeast blackout event. Other data points include the 2011 Southwest blackout and 2019 PSPS outages in the SCE service area. • SCE has incorporated a new targeting multiplier to its Safety index which amplifies the score based on an internal analysis of two population sets, Access and Functional Needs (AFN) customers and Non-Residential Critical Infrastructure (NRCI). SCE collects data for a subset of this population annually, which include MBL, Critical Care, Low Income, limited English proficiency, and self-certified vulnerable customers who are served by SCE. At the circuit level, SCE developed both an AFN and NRCI score to incorporate the level of support that an individual or entity would need in an emergency event or a PSPS event, in the case of an AFN customer. | 2021-03-03 | 2021-03-09
MGRA-SCE-006 | 010 | Please provide data and/or calculation showing the dependency of FPI 2.0 on wind speed. | The current FPI references a matrix to calculate the weather score which is based on wind speed (miles per hour at 20 feet) and dew point depression (degrees F). Dew point depression is a way to measure how dry the air is near the ground. The limitation to the current FPI is that it does not account for wind speeds that are greater than 29 mph and dew point depressions that are greater than 50 since anything above these values would be assigned a “6” no matter the level of exceedance in both variables. FPI 2.0 will have no upper boundaries because it will not be utilizing a matrix. The weather score in FPI 2.0 will be calculated using one of the following formulas: FPI 2.0weather = (WindSpeed^2)*(Dew Point Depression) or (WindSpeed^2)*(Vapor Pressure Deficit) Testing and evaluating these formulas over both a historical period and in real time will determine which performs better. Both versions of the equation put the same emphasis on the wind speed which is why that variable is squared. It has been observed that stronger winds can overcome fire mitigating factors such as moisture in the air or in the vegetation, so it is important that wind speeds be the dominant factor in the FPI 2.0 formula. In addition, this new formula will account for winds at any strength with no upper boundary limitations. | 2021-03-03 | 2021-03-08
WSD-SCE-003 | 001 | On the 3/3/2021 utility call, SCE clarified that Table 11, field 3.a in “SCE Tables 1-12 .xlsx" (Critical infrastructure impacted by PSPS) should have been 5768 for 2019 and 5123 for 2020. Confirm that Table 11, field 3.a. is now correct, if not, provide accurate numbers – Table | Table 11 is not correct. For 2019 actual, the figure should be 5,868. SCE’s Feb. 5, 2021 submission inadvertently included an incorrect value for 2019. For 2020, the figures for Q1, Q2 and Q3 figure are correct; however, the Q4 figure should be updated to 5,128. SCE’s Feb. 5, 2021 submission included values for Q4 2020 that were still being reviewed. As a result of completing our validation process, the Q4 2020 figure was updated to 5,128. | 2021-03-04 | 2021-03-09
WSD-SCE-003 | 002 | SCE's reported cycle spend has conflicted across submissions, and WSD requires SCE to remedy this issue as detailed below. Provided that the WSD has attempted to obtain this information for several weeks, if SCE fails to provide the WSD with accurate and consistent information, or explanations for any discrepancies, the WSD will factor this into its review of SCE’s 2021 WMP and pursue further action as necessary. Context - The following outlines the timeline of data collection efforts for SCE spend data from the most recent reporting in 2020 (WMP revision 02) to the most recent reporting in 2021. • In its 2020 WMP submission (second revision), SCE reported a total 2020-22 planned cycle spend of 4.512B, calculated by summing all rows titled "2020-2022 plan total" in column C of tables 21-30 from the 2020 WMP. • In its 2021 WMP submission on February 5th, SCE reported a total 2020-2022 cycle planned spend of $6.751B, calculated by summing columns (U+V+Y+Z+AC+AD) as reported in table 12 " SCE Tables 1-12.xlsx" • In the first utility call on 2/10/2021, SCE explained that the $6.751B reported spend in the 2021 WMP included all initiative spend, both within and outside of “high fire risk areas” or “HFRA” (referred to as 2021 cycle reported). This reporting method differed from the $4.512B spend SCE reported in 2020, which SCE only included spend in HFRA (referred to as 2020 cycle reported). • To obtain comparable data across submissions, the WSD submitted a follow-on data request on 2/18/2021, requesting SCE to split the 2021 cycle reported $6.751B into HFTD and non-HFTD, and provide the non-HFTD portion of the 2020 cycle reported. o On 2/23/2021 SCE responded to the data request by providing “WSD-SCE-001 Q1 Data request SCE 2021 Table 12_v02 20210223.xlsx”, which split 2021 cycle reported into HFTD and non-HFTD in columns AS - BP. However, SCE did not provide 2020 cycle reported in HFTD or non-HFTD, as required in columns U-AR • Summing columns (AU+AV+BC+BD+BK+BL) in “WSD-SCE-001 Q1 Data request SCE 2021 Table 12_v02 20210223.xlsx” SCE's 2021 cycle reported spend was $6.753B, which is slightly inconsistent with the $6.751B reported Issue • On 3/1/2021, after still not receiving data requested on 2/18/2021, the WSD found what it believes to be SCE's 2020 cycle reported in HFTD and non-HFTD on SCE's website in a file titled "002_Data request SCE 2021 Table 12_20210223.xlsx" o In "002_Data request SCE 2021 Table 12_20210223.xlsx" SCE provided a territory-wide (HFTD SCE's reported cycle spend has conflicted across submissions, and WSD requires SCE to remedy this issue as detailed below. Provided that the WSD has attempted to obtain this information for several weeks, if SCE fails to provide the WSD with accurate and consistent information, or explanations for any discrepancies, the WSD will factor this into its review of SCE’s 2021 WMP and pursue further action as necessary. Context - The following outlines the timeline of data collection efforts for SCE spend data from the most recent reporting in 2020 (WMP revision 02) to the most recent reporting in 2021. • In its 2020 WMP submission (second revision), SCE reported a total 2020-22 planned cycle spend of 4.512B, calculated by summing all rows titled "2020-2022 plan total" in column C of tables 21-30 from the 2020 WMP. • In its 2021 WMP submission on February 5th, SCE reported a total 2020-2022 cycle planned spend of $6.751B, calculated by summing columns (U+V+Y+Z+AC+AD) as reported in table 12 " SCE Tables 1-12.xlsx" • In the first utility call on 2/10/2021, SCE explained that the $6.751B reported spend in the 2021 WMP included all initiative spend, both within and outside of “high fire risk areas” or “HFRA” (referred to as 2021 cycle reported). This reporting method differed from the $4.512B spend SCE reported in 2020, which SCE only included spend in HFRA (referred to as 2020 cycle reported). • To obtain comparable data across submissions, the WSD submitted a follow-on data request on 2/18/2021, requesting SCE to split the 2021 cycle reported $6.751B into HFTD and non-HFTD, and provide the non-HFTD portion of the 2020 cycle reported. o On 2/23/2021 SCE responded to the data request by providing “WSD-SCE-001 Q1 Data request SCE 2021 Table 12_v02 20210223.xlsx”, which split 2021 cycle reported into HFTD and non-HFTD in columns AS - BP. However, SCE did not provide 2020 cycle reported in HFTD or non-HFTD, as required in columns U-AR • Summing columns (AU+AV+BC+BD+BK+BL) in “WSD-SCE-001 Q1 Data request SCE 2021 Table 12_v02 20210223.xlsx” SCE's 2021 cycle reported spend was $6.753B, which is slightly inconsistent with the $6.751B reported Issue • On 3/1/2021, after still not receiving data requested on 2/18/2021, the WSD found what it believes to be SCE's 2020 cycle reported in HFTD and non-HFTD on SCE's website in a file titled "002_Data request SCE 2021 Table 12_20210223.xlsx" o In "002_Data request SCE 2021 Table 12_20210223.xlsx" SCE provided a territory-wide (HFTD and non-HFTD) 2020 cycle reported of $4.473B, which was calculated by summing columns (W+X+AE+AF+AM+AN) • This is less than the HFRA-only 2020 cycle reported of $4.512B, as reported in SCE’s 2020 WMP (second revision), despite including spend across SCE's entire territory o In "002_Data request SCE 2021 Table 12_20210223.xlsx" SCE provided an HFTD 2020 cycle reported of $3.824B, which was calculated by summing columns (AL+AK+AD+AC+V+U) • This is $0.688B less in WMP cycle spend than was reported in SCE's 2020 WMP for HFRA spend (4.512B). However, SCE stated during 2/17 utility content call that HFTD was equivalent to HFRA • Additionally, on the 2/26/2021 utility call, SCE stated its reported cycle spend for Category C – “Grid design and system hardening” had increased by $100M from its 2020 cycle reported to 2021 cycle reported. However, WSD finds a $700M decrease in planned cycle spend from 2020 cycle reported to 2021 cycle reported. 2020 cycle reported spend in Grid Design and system hardening was calculated by summing all rows titled “2020-2022 plan total” in column C of table 23 from the 2020 WMP. 2021 cycle reported spend in Grid design and system hardening was calculated by summing columns (U+V+Y+Z+AC+AD) for all rows labeled “Grid Design & System Hardening” in column C as reported in table 12 " SCE Tables 1-12.xlsx" Remedy • Below is WSD’s understanding of SCE’s total cycle spend and Grid design and system hardening cycle spend prior to 3/1. The WSD requests SCE to confirm whether these values are correct. If these values are incorrect, indicate which submission of 2020 reported spend the WSD should use (by providing the appropriate file name) and how to calculate the correct values (with reference to appropriate rows/columns in the identified file), as requested in the table below. Provided that the WSD has attempted to obtain this information for several weeks, SCE is requested to provide the above information by 3/9/2021. If SCE fails to provide the WSD with accurate and consistent information, or explanations for any discrepancies, the WSD will factor this into its review of SCE’s 2021 WMP and pursue further action as necessary. | For SCE’s response to this data request, please see Excel file entitled “WSD-SCE-003-002_20210309.xlsx.” The following tabs can be found within file “WSD-SCE-003-002_20210309.xlsx:” Summary – States the total cycle spend reported in the 2020 WMP and the 2021 WMP by region of SCE territory and by WMP activities and non-WMP programs • WMP Forecast Comparison – Compares the forecast between the 2020 WMP (revision 2) and the 2021 WMP and provides variance explanations at the WMP Activity level • WMP Program Reconciliation – Reconciles the WMP Activities in the 2020 WMP with the 2021 WMP • Grid Hardening Reconciliation – Reconciles the WMP Activities related to Grid Design and System Hardening in the 2020 WMP with the 2021 WMP (similar to WMP Program Reconciliation tab, but focused on Grid Design and System Hardening) • DATA_Tables 21-30 Rev2 – Consolidates tables 21-30 from the 2020 WMP (revision 2) into a single tab • Tables 21-30 – These tabs are from the 2020 WMP (revision 2) and are for reference Notes and formulas appear throughout the file for your reference. | 2021-03-04 | 2021-03-09
WSD-SCE-003 | 003 | Regarding your response in a data request received from SCE on 2/23/21: “Veg Mgmt: Line Clearing: Increase in forecast driven by: Inclusion of SB 247 and related rate increases ($135M annually) unknown at the time of filing of the 2020 WMP.” (Data Request WSD-SCE-001, Q. 003) a. Provide where in the 2021 SCE WMP the $135M annual costs can be found? b. Identify which initiatives, with section and page number references, that these annual costs apply to. c. Break down the costs within the above identified initiatives which total $135M annually. d. Clarify which years (2020, 2021, or 2022) are included in the "$135M annually." e. Identify where in its 2021 WMP SCE explains its rationale and justification for the vegetation management cost increases associated with SB 247. | The estimated SB 247 $135M annual impact figure that SCE provided in response to WSD-SCE-001, Question 1 and in oral explanations to the WSD during our weekly meetings was based on a previous estimated figure regarding the annual impact of the vegetation management cost increases due to SB 247 in total (systemwide). SB 247 went into effect beginning January 1, 2020. As a result, SCE was required to adjust the contract rates for its vegetation management contracts which didn’t occur until January / February 2020 and had to pro-rate these increases back to January 1, 2020. Because these analyses and adjustments were ongoing at the time SCE finalized its 2020 WMP, the SB 247 contract rate cost increase was not accounted for in its 2020 WMP. These adjustments resulted in various contract rate increases across various types of work, e.g., pre- and post-SB 247 contract rate increases were different for different types of work and vendors. The SB 247 $135M annual increase was based on a previous simplified analysis of the total, systemwide SB 247 cost impact. SCE has since re-assessed the vegetation management cost forecasts included in its 2020 WMP and 2021 WMP Update and was able to estimate the SB 247 contract rate cost increase for its Vegetation Clearance (7.3.5.20) initiative for HFRA. In the attached file, SCE explains the variances for each Vegetation Management initiative in the 2020 and 2021 WMPs. This analysis includes some remapping of Vegetation Management costs in order to explain the variances. Additionally, SCE has identified a few errors that are described and for which SCE will revise through a subsequent 2021 WMP Update revision submission. The analysis is attached (See “WSD-SCE-003_Q3_VM Cost Reconciliation.xlsx”) and is the basis of our responses below. a) Table 12 of the Q4 2020 Quarterly Data Report (QDR) includes recorded costs for 2020 and forecast costs for 2021 and 2022 for SCE’s wildfire and non-wildfire initiatives. Vegetation Management recorded and forecast costs are included in Table 12. SB 247 contract cost increases impacted three Vegetation Management initiatives: Vegetation Clearances (7.3.5.20), Hazard Tree Mitigation Program (7.3.5.16.1), and Dead and Dying Tree Removal (formerly DRI) (7.3.5.16.2). The attached file includes an estimated SB 247 contract rate cost increase for Vegetation Clearances in HFRA of $83M for 2020, $66M for 2021, and $68M for 2022. The impact of the SB 247 contract rate increase for HTMP and Dead and Dying Tree Removal was not estimated. b) As noted above, the SB 247 contract rate cost increase impacts the following initiatives: • Vegetation Clearances (7.3.5.20) • HTMP (7.3.5.16.1) • Dead and Dying Tree Removal (7.3.5.16.1) c) Please see the attached Vegetation Management Reconciliation Excel file that includes the SB 247 contractor rate cost impact for Vegetation Clearances in HFRA. d) Please see the attached Vegetation Management Reconciliation Excel file that includes the 2020, 2021, and 2022 breakout for the SB 247 contractor rate cost increase for Vegetation Clearances in HFRA. e) SCE’s 2021 WMP Update, similar to its 2019 and 2020 WMP, does not describe cost details nor include cost justification for its wildfire initiatives consistent with the statutory, CPUC, and WSD requirements for WMPs. Cost recovery will occur in a utilities’ General Rate Case or other application. Furthermore, WSD-011 does not include any requirement to justify cost increases of WMP initiatives. However, we are providing the cost details in the attached file with explanations of the changes. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 001 | Has SCE set a target date to complete its planned 2021 vegetation management (VM) work in HFTD areas? a) If yes, please provide the target date. b) If no, please explain why not. | a) All 2021 Vegetation Management (VM) work in HFRA is performed in accordance with an annual schedule that separates work into monthly work assignments (January through December) for SCE’s vegetation contractors. Inspections scheduled for each program are typically required to be completed within 30 days of the month the work is assigned, and all prescriptions resulting from the inspections are typically performed the following month for locations with no work restrictions, with the exception of prescriptions for heavy tree removal programs (Hazard tree and Dead and Dying tree removal) which may take 180 days to complete once access and authorization for the removal has been granted. Notwithstanding this, 2021 HFRA work is expected to be completed by December 31, 2021 except as noted above. b) Not Applicable – refer to part (a) | 2021-03-04 | 2021-03-08
CalAdvocates-SCE-2021WMP-09 | 002 | Please describe the pay structure for vegetation management (VM) pre-inspection contractors. For example, are these contractors paid by a fixed monthly retainer, by the hour, by the mile of work completed, etc.? | Pre-Inspection contractors are paid for their primary work on Fixed Annual Lump Sum divided into monthly values. Pre-inspection contracts also have Time and Material rates for non-primary work such as emergency response, supplemental response outside their awarded area, Priority 1 standby, and large distribution line construction project support. | 2021-03-04 | 2021-03-08
CalAdvocates-SCE-2021WMP-09 | 003 | a) Please describe the pay structure for vegetation management (VM) contractors. For example, are these contractors paid by a fixed monthly retainer, by the hour, by the mile of work completed, etc.? b) Does the incentive structure for VM contractors include provisions for nonpayment or other penalties for work that fails quality control? c) If the answer to part (b) is yes, please explain all such provisions. | a) The majority of VM trimming contractors are paid for their primary work on Fixed Unit Rate, per tree trimmed. Pre-Inspection contractors are paid for their primary work on Fixed Annual Lump Sum divided into monthly values. There is one trimming and pre-inspection contractor who is also compensated on Fixed Lump Sum as a pilot for current round of contracts. Both Trimming and Pre-inspection also have Time and Material rates for non-primary work such as emergency response, supplemental response outside their awarded area, or large distribution line construction project support. a. There is no "incentive structure" in the contracts, there is standard "consideration" or exchange of value for value, which include provisions for customer actions, including nonpayment, if the contractors do not meet their service requirements, including failure of quality control. Additionally, contractors must correct pruning at no additional cost when quality control identifies a deficiency with a pruned tree. c. Vegetation Line Clearing contracts are managed by scorecards that include Quality metrics. If those quality levels aren't met, the contractors may be put into a series of control stages with increasing negative actions including loss of opportunity to bid on future work while in control stage, surrendering of current work, or termination. Regarding non-payment, quality of work (i.e., Standard of Performance) is considered a material obligation of the contractor and, therefore, the Master Agreement allows for violations of these obligations to be considered a breach of contract or contractor default. The Master Agreement provisions that address this are typically found under the sections entitled, Non-Conformance Remedies, Disputed Charges and Right of Set-Off which, by way of explanation, are provided below: Non-Conformance Remedies. Upon redelivery of the Service or Deliverable to Edison, Edison shall review the Service or Deliverable and advise Contractor within a reasonable time period whether it conforms to the Service or Deliverable Requirements. After two attempts by Contractor to correct the Service or Deliverable, if Edison determines the Service or Deliverable fails to conform to the Service or Deliverable Requirements, the Service or Deliverable shall be conclusively deemed to not conform to the Service or Deliverable Requirements and Edison shall be entitled, at its option, to either: (A) Accept the non-conforming Service or Deliverable, subject to reduction in the applicable charges payable, as determined (1) by agreement of the Parties, or (2) in accordance with the procedures in Section 19.3 (“Dispute Resolution”) of this MSA, if the Parties cannot agree to the amount of reduction within 30 days after Edison requests a reduction; or (B) Reject the Service or Deliverable and receive a refund of any amounts Edison paid Contractor for that non-conforming Service or Deliverable; or (C) Exercise its remedies under Section 16 (“Term and Termination”) of this MSA due to a Contractor Event of Default. Disputed Charges. Edison shall pay undisputed charges when these payments are due under the Agreement. Edison has the right to withhold payment of particular charges that Edison disputes in good faith, pending the resolution of the dispute, and Edison will provide Contractor with notice of the amounts being withheld and the reasons for the dispute. Pending resolution of the issues, Edison’s non-payment of the disputed charges shall not be deemed a breach of the Agreement by Edison and shall not entitle Contractor to suspend or delay its furnishing of the Services or Deliverables. Right of Set-Off. With respect to any amount to be paid by Edison under the Agreement, Edison may (without liability or notice obligations) deduct, withhold or set off from this amount any amount Contractor owes Edison. | 2021-03-04 | 2021-03-08
CalAdvocates-SCE-2021WMP-09 | 004 | Table 1 of SCE’s non-spatial WMP data tables includes data on “Number of spans inspected where at least some vegetation was found in non-compliant condition in HFTD” (line 2.b.i) and “Number of spans inspected for vegetation compliance in HFTD” (line 2.b.ii). a) State the average span length that SCE used to calculate the metrics in WMP Table 1. b) State the total number of circuit-miles you inspected for vegetation in 2019. c) Disaggregate the total in part (b) by VM initiative or type of inspection (for example, routine inspections, canyon patrols, at-risk circuit patrols, and Operation Santa Ana patrols). d) State the total number of circuit-miles you inspected for vegetation in 2020. e) Disaggregate the total in part (d) by VM initiative or type of inspection (for example, routine inspections, canyon patrols, at-risk circuit patrols, and Operation Santa Ana patrols). | a) Average Span Length in HFTD = The average span length for both Distribution and Transmission poles/towers in HFTD is 0.118725 Circuit miles. Calculation for 2.b.i Circuit Miles Inspected X (1-conformance rate) Average Span Length HFTD Where Circuit miles Inspected = # of circuit miles inspected as part of vegetation management program Conformance rate = % rate of the circuit miles inspected where non-compliant condition was found Average Span Length HFTD = The average span length for both Distribution and Transmission poles/towers in HFTD expressed in circuit miles Calculation for 2.b.ii Circuit Miles Inspected Average Span Length HFTD Where Circuit miles Inspected = # of circuit miles inspected as part of vegetation management program Average Span Length HFTD = The average span length for both Distribution and Transmission poles/towers expressed in circuit miles b) Vegetation Management crews inspect all circuits in SCE’s service area annually for SCE’s line clearing program. In 2019, approximately 52,000 circuit miles were inspected by SCE VM crews. Of the approximate 52,000 circuit miles, approximately 14,000 circuit miles were in HFRA. c) When documenting SCE’s response to WMP Table 1 line items 78 through 81, SCE only considered non-compliant conditions to published standards such as GO 95 Rule 35 and FAC-003-4 which apply to SCE’s line clearing program and not its identified VM initiatives. Additionally, canyon patrols, at-risk circuit patrols, and Operation Santa Ana patrols were not provided in the original Table 1 calculation due to the difficulty in aggregating mileage totals and associated non-compliant findings specific to each of the activities. Based on the above, disaggregation for response to (c) is not applicable. d) Circuit miles between 2019 and 2020 did not change. SCE VM crews inspected the same circuit miles. e) See response to (c) | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 005 | The following questions relate to Table 1 of the non-spatial WMP data tables. All questions specifically concern inspections of distribution facilities in HFTD areas. For purposes of this data request, “high-priority findings” mean Level 1 and Level 2 inspection findings. Provide all procedures, manuals, job aids, and standards that SCE uses to implement distribution line inspections. | Please see the attached files. Additionally, please see SCE’s Response to the 2020 WMP Class B Deficiency Action Statements, Guidance-7, Action SCE-6. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 006 | The following questions relate to Table 1 of the non-spatial WMP data tables. All questions specifically concern inspections of distribution facilities in HFTD areas. For purposes of this data request, “high-priority findings” mean Level 1 and Level 2 inspection findings. For each type of detailed or “other” inspection that you perform on distribution facilities in HFTD areas, please answer the following questions: a) Please list the five most common types of high-priority findings identified in these inspections. b) How many personnel are involved in each inspection? c) In 2020, how many person-hours were typically required to complete an inspection of one distribution pole and the equipment on it? d) In 2020, how many person-hours were typically required to inspect one circuit-mile? e) How many qualified personnel do you currently have to perform these inspections? f) Of the personnel identified in part (e), how many are direct employees of SCE and how many are contractors? | a) The table below shows the five most common high priority findings identified by each inspection type. b) - f) The table below shows the responses for each inspection type ¹ SCE does not track inspections by circuit mile (except for Infrared inspections). The person hours from part c were used to estimate the equivalent circuit miles. ² This activity is performed by a contractor. SCE does not have detailed information on the resources and person hours per inspection. ³ This activity is performed by a contractor at a unit rate. SCE does not have information on the person-hours per inspection. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 007 | The following questions relate to Table 1 of the non-spatial WMP data tables. All questions specifically concern inspections of distribution facilities in HFTD areas. For purposes of this data request, “high-priority findings” mean Level 1 and Level 2 inspection findings. For distribution High Fire Risk-Informed (HFRI) Inspections and Remediations, SCE states that “the frequency of inspections varies by the location specific risk within SCE’s HFRA and emergent conditions.” List and explain in detail the criteria SCE uses to determine the frequency of HFRI inspections, including the location-specific risks and emergent conditions considered and the relationships between the location-specific risks and emergent conditions to the frequency of inspections. | SCE’s wildfire risk model has two main elements: The Probability of Ignition (POI) and the consequence of a wildfire (i.e., it takes into account both sides of the “risk bowtie”). SCE’s POI model was developed to estimate the probability of ignition at each specific structure location. The consequence model developed by Technosylva was also created at a location specific level such that the consequence score reflects the location specific fire damage potential in the event there is an ignition at that location. When SCE develops its annual inspection plan, both the probability and consequence of ignition are considered. SCE created a 4 x 4 matrix with one dimension of the matrix representing four levels of POI risk and the other dimension representing four levels of consequence. The four levels are made up of 25 percentile groupings. For example, the Level 1 POI includes the top 25% of POI structure scores. Similarly, Level 4 includes the lowest 25% of POI structure scores. Each structure is mapped to a box in the matrix based on its POI level and consequence level showing the risk distribution of the structures. The structures mapped to red boxes will be inspected in 2021. The structures mapped to the blue boxes remain on the minimum compliance inspection schedule of every 5 years. In developing the annual inspection plan, SCE balances risk reduction, resource availability and costs. In addition, any structures due for a compliance inspection in 2021, regardless of which box they are mapped to, will be included in 2021 scope. The matrix below is also included in SCE’s 2021 WMP update on page 240. Visualization of Distribution Structures Risk Analysis In addition to the risk analysis described above, in 2020, SCE identified emergent risk during the fire season due to high winds, dry conditions and accumulation of dry fuel, which were above average fire weather conditions. SCE identified 17 Areas of Concern (AOCs) in 2020 where overhead structures were re-inspected prior to fire season to identify changes in asset condition that could pose ignition risks. SCE’s Fire Science team considered fire history, weather conditions, fuel type, exposure to wind, and egress to determine these AOCs. SCE’s 2021 inspection forecast includes 30,000 potential additional distribution inspections for AOCs identified in 2021, though the actual inspections will depend on observed emergent fire risks. Depending on the volume of work driven by emergent risks, resource availability, and execution capacity, SCE might have to reprioritize the total volume and location of inspections. | 2021-03-04 | 2021-03-08
CalAdvocates-SCE-2021WMP-09 | 008 | The following questions relate to Table 1 of the non-spatial WMP data tables. All questions specifically concern inspections of distribution facilities in HFTD areas. For purposes of this data request, “high-priority findings” mean Level 1 and Level 2 inspection findings. This table shows rates of high-priority findings per mile of detailed inspections in HFTD areas, based on Table 1 of SCE’s 2021 non-spatial WMP data tables. a) Explain the factors that resulted in a much lower rate of high-priority findings per mile on detailed inspections in 2019 than in any other year from 2015 to 2020. b) Explain the factors that resulted in significantly fewer high-priority findings per mile on detailed inspections in 2020 than in 2015 through 2018. | Upon further review of the data submitted in the WMP, an error was found on how the numbers for both Level 1 and 2 findings in HFTD for detailed inspections – Distribution lines were produced. For 2018-2020, both Level 1 and 2 findings in HFTD for detailed inspections – Distribution lines were undercounted. Counts of Level 1 and level 2 findings due to detailed inspections were inadvertently counted in all Level findings due to both “other inspections” and “patrol inspections” type inspections. This error occurred because the flag stating the findings were due to Enhanced Detailed Inspections (EOI) was incorrectly used. As such, large counts of findings for all levels were inadvertently counted in both “other inspections” and “patrol inspections.” The table below shows the updated Level 1 and level 2 findings and the calculated findings per miles of detailed inspections. The updated numbers are in Red. a) After the update seen above, (in red) 2019 is actually slightly higher than the average find rate for 2015-2018, but the 2019 find rate increased significantly as compared to the average 2015-2017. This significant increase can be attributed to inspections prioritizing the highest risk areas during the start of the EOI program. This is because the focus of the program was the highest risk areas and the EOI program increased inspection focus on specific types of hardware and equipment on the distribution system to minimize wildfire risk. The increased focus based on specific types of hardware and equipment performance on the distribution system resulted in an increased find rate. b) After the updates seen above, (in red) 2020 increased slightly, but is still below the average for 2015-2018. The lower find rate can be attributed to the change in detailed inspection cycles and additional detailed inspection programs. The high fire risk informed inspection program shortened the time-period assets are re-inspected based on risk, compared to the years 2015-2018. Additionally, in 2020, assets may have been inspected by multiple detailed inspection programs such as aerial and/or areas of concern, resulting in an increased inspection circuit mile count and decreased findings count. The combination of detailed inspection cycle times and the additions of other detail inspection programs resulted in a lower find rate in 2020. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 009 | The following questions relate to Table 1 of the non-spatial WMP data tables. All questions specifically concern inspections of distribution facilities in HFTD areas. For purposes of this data request, “high-priority findings” mean Level 1 and Level 2 inspection findings. This table shows the number of Level 3 findings, based on Table 1 of SCE’s 2021 non-spatial WMP data tables. Explain the factors that resulted in a sharp increase in Level 3 findings for all asset patrols and inspections in 2019, followed by a sharp decrease in 2020. | During 2019, SCE’s Enhanced Overhead Inspection (EOI) program increased inspection focus on specific types of hardware and equipment on the distribution system to minimize wildfire risk. The increased focus was warranted based on specific types of hardware and equipment performance on the distribution system, e.g., maximizing animal protection, replacing automatic primary splices, and minimizing liquid primary fuse locations of the distribution system. The enhanced focus on the described hardware and equipment increased priority 3 notifications significantly during the initial EOI program launch. Then, moving forward in 2020, SCE decided to recognize specific types of hardware and equipment findings as programmatic opportunity scope and not continue to create notifications for remediation. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 010 | The following questions relate to the use of live field observers (LFO) immediately prior to and during a PSPS event. What information is gathered by the field observers beyond noting possible signs of failure or potential damages to SCE’s assets? | SCE’s live field observers gather several key live weather data points. These include sustained and gust wind speeds, relative humidity and other conditions like the presence of lightning, precipitation and snow. These observers also provide a valuable source of general situational awareness for any local conditions or considerations that should be relayed back to SCE’s Incident Management Team. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 011 | The following questions relate to the use of live field observers (LFO) immediately prior to and during a PSPS event. Does SCE instruct its field observers to make recommendations beyond verifying the ability of a circuit to withstand incoming weather? If so, what types of other recommendations do field observers make? | SCE’s live field observers make recommendations on operations like switching and rolling load from one circuit to another. Their local SME knowledge can sometimes provide valuable insight beyond SCE’s circuit switching playbooks and can lead to opportunities to reduce customers and circuits impacted. Ultimately, if a live field observer sees an imminent threat, they also have the authority to contact the switching center directly and request immediate de-energization. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 012 | The following questions relate to the use of live field observers (LFO) immediately prior to and during a PSPS event. Have SCE’s field observers ever recommended, immediately prior to a potential PSPS, that a circuit that is potentially within the scope of a PSPS not be de-energized? If so, what is the number of instances in which SCE Incident Commanders followed that recommendation? | Yes, SCE regularly solicits de-energization input from live field observers. SCE does not track instances when an observer recommends against de-energization, which is not an uncommon occurrence. SCE’s Incident Management Team follows these recommendations when they believe it is safe to do so, but may also proceed with de-energization if that is appropriate in their professional judgment. For example, a live field observer may be observing conditions safe enough to warrant continued operation in that particular location of the circuit, but other areas of the circuit may be experiencing higher or more damaging winds. | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 013 | The following questions relate to the use of live field observers (LFO) immediately prior to and during a PSPS event. Has SCE ever used the information gathered by field observers prior to a PSPS event to modify wind speed triggers for a circuit that is potentially within the scope of a PSPS? If so, describe examples of this decision-making process and examples of when this decision-making process was used, including the date, location, and the information gathered or communicated by the field observer. | SCE does not use information from live field observations to modify wind speed triggers. Live field observations do not result in modification of wind speed triggers because SCE does not modify triggers in a particular event. Rather, SCE establishes the triggers prior to events based on circuit characteristics. However, information from other patrols is sometimes used to modify wind speed triggers. For example, SCE regularly utilizes PSPS pre-patrols or other adhoc patrols to verify completed grid hardening work that would warrant possible adjustments to wind speed triggers. If SCE completes a work order that results in a PSPS circuit or isolatable circuit segment being fully installed with covered conductor, a patrol of that circuit can confirm circuit conditions and allow SCE’s subject matter experts to create new wind speed triggers based off of the National Weather Service’s High Wind Warning (40 mph sustained winds and/or 58 mph wind gusts). | 2021-03-04 | 2021-03-09
CalAdvocates-SCE-2021WMP-09 | 014 | The following questions relate to the use of live field observers (LFO) immediately prior to and during a PSPS event. In its 2021 WMP, SCE states that: SCE considers the National Weather Service Wind Advisory levels (defined as 31 mph sustained wind speed and 46 mph gust wind speed) and the 99th percentile of historical wind speeds in the area to set activation thresholds. However, in a response to the Acton Town Council’s discovery request, SCE states that: After determining the modified multiplier, we must determine if it’s to be applied to the circuit’s “Wind/Gust Threshold” or its “99th Percentile” threshold. The “Wind/Gust Threshold” is determined by historical wind-related outages and the “99th Percentile” threshold is determined by the 99th percentile of historical wind speeds recorded for the circuit. Is the Wind/Gust Threshold the same as SCE’s use of NWS Wind Advisory level of 31 mph (sustained) and 46 mph (gust)? If not, explain which criteria SCE currently uses. | In almost all cases, SCE uses the lower of the NWS Wind Advisory level of 31 mph (sustained) and 46 mph (gust) or a circuit’s 99th percentile wind speed to perform PSPS notifications and Incident Management Team activation. However, roughly a dozen SCE distribution circuits have outage-informed thresholds that are marginally lower than the NWS Wind Advisory level of 31 mph (sustained) and 46 mph (gust). These circuits have sustained concerning historical outages at wind speeds lower than the NWS Wind Advisory level and have had their threshold capped until completed maintenance has demonstrated the ability for each circuit to sustain higher wind speeds. An example of this treatment was seen on the Shovel circuit in Acton in 2020. SCE was able to raise Shovel’s outage-informed threshold of 25 mph (sustained) or 40 mph (gust) to the NWS Wind Advisory level. This occurred in late 2020 after confirming that key outstanding maintenance was completed and that the circuit was able to withstand NWS Wind Advisory level wind speeds without mechanical failure. | 2021-03-04 | 2021-03-09
TURN-SCE-004 | 001 | Regarding the circuit miles deenergized during 2020 PSPS events: a. Had SCE already installed covered conductor on any of the miles experiencing a PSPS event? b. If the answer to subpart a above is yes, what percentage of the deenergized miles had covered conductor installed? | a) Yes, SCE had already installed covered conductor on some of the miles that experienced a 2020 PSPS event. b) Because SCE would have to analyze historical snapshots of covered conductor installation status on a circuit-by-circuit basis for each de-energization point in time, it would take SCE much longer to analyze and derive the information requested than is granted for WMP data requests. Instead, SCE is providing the attached spreadsheet, which shows, as of year-end 2020, the miles of covered conductor installed for each circuit that experienced a PSPS de-energization in 2020. This spreadsheet also provides the number of bare overhead miles for each circuit so that a percentage of overhead HFRA circuit miles that had covered conductor installed can be derived. Because this list is generated using 2020 year-end data, some circuits will show more covered conductor installed than was installed at the time of their PSPS de-energization(s). | 2021-03-05 | 2021-03-10
TURN-SCE-004 | 002 | Is the covered conductor proposal included in SCE’s wildfire mitigation plan identical to the covered conductor proposal included in SCE’s 2021 General Rate Case, A.19-08-013? To the extent that the proposals are different please identify any differences. | SCE interprets this question as referring to whether the volume of circuit miles included for 2021 and 2022 in SCE’s 2021 WMP Update are the same as the volume of circuit miles requested in SCE’s 2021 GRC Track 1 filing for those same years. With this context, yes, the covered conductor proposals are aligned. SCE’s 2021 GRC proposes 1,400 circuit miles in 2021 and 1,600 circuit miles in 2022 and SCE’s 2021 WMP Update proposes 1,000 – 1,400 miles in 2021 and 1,600 miles in 2022. | 2021-03-05 | 2021-03-10
CalAdvocates-SCE-2021WMP-10 | 001 a-d and g-h | Regarding SCE’s program of personnel monitoring areas of electric lines and equipment in elevated fire risk conditions (WMP Section 7.3.2.5): A) Of the 1,904 patrols performed under that heading, what number were pre-event patrols? B) Of the 1,904 patrols performed under that heading, what number were restoration patrols? C) Does the program include any patrols other than pre-event patrols and restoration patrols? D) If the answer to (C) is yes, please describe those patrols. G) Please provide an estimate of the average duration (in hours and minutes) of a pre-event patrol described under Section 7.3.2.5. H) Please provide an estimate of the average duration (in hours and minutes) of a restoration patrol described under Section 7.3.2.5. | A) 1,461 of the patrols performed were pre-patrols. B) 443 of the patrols performed were post-patrols. C) SCE’s live field observations (LFOs) are also included in the program work under “personnel monitoring areas of electric lines and equipment in elevated fire risk conditions” but are not captured in the count of 1,904 patrols. D) Please see Section 7.3.2.5 of SCE’s 2021 WMP Update for a description of SCE’s live field observations. G) Pre-patrol average duration in 2020 was 3 hours and 37 minutes. H) Post-patrol average duration in 2020 was 6 hours and 31 minutes. | 2021-03-08 | 2021-03-11
CalAdvocates-SCE-2021WMP-10 | 001 e-f | Regarding SCE’s program of personnel monitoring areas of electric lines and equipment in elevated fire risk conditions (WMP Section 7.3.2.5): E) Do the program cost estimates in WMP Table 12 include any work other than patrols? (For example, repair of assets identified as dangerous during a patrol) F) If the answer to (E) is yes, please describe the nature of any other work that is included in that program for purposes of cost reporting in SCE’s 2021 WMP Update. | E) No, no other costs (e.g., repair materials or labor) are included in the program cost estimates. F) N/A | 2021-03-08 | 2021-03-11
CalAdvocates-SCE-2021WMP-10 | 002 | In SCE’s Deficiency Action Statement on a lack of detail regarding Pole Loading Assessment Program (Supplemental Filing at page 356), SCE cites as reasons for the deficiency five complicating factors, including (1) customers denying access to property; (2) customers being unavailable to grant access to property; (3) access issues due to COVID-19; (4) weather and fires complicating access to poles; and (5) hazardous terrain unrelated to weather and fires. Of the 860 assessments forecast that were not completed due to the above complications, please provide the percentage caused by each of the stated complications (e.g., unavailable customers prevented 10% of uncompleted assessments). If the percentages do not total 100, please describe any other complications that contributed to the uncompleted assessments. | SCE presently forecasts 929 pending assessments rather than the 860 previously reported in the Deficiency Action Statement. New High Fire Risk Area poles were identified based on updated source data from January 14, 2021. The following is the current percentage breakdown by factor: 44% pending Pole Loading Program field assessment, 32% data validation, 23% hazardous terrain unrelated to weather and fires, and 1% customers denying access to property. | 2021-03-08 | 2021-03-10
CalAdvocates-SCE-2021WMP-11 | 001 | Table 7.1 of SCE’s non-spatial WMP data tables includes data on “Transformer damage or failure – Distribution” (line 18n). According to that table, the number of outages caused by distribution transformer damage or failure increased from 2,489 in 2019 to 3,405 in 2020. a) Explain the factors that account for this increase in transformer-related outages in 2020, compared to 2019. b) What is the minimum age of the transformers that failed in 2020 in the line 18n data? c) What is the maximum age of the transformers that failed in 2020 in the line 18n data? d) What is the mean age of the transformers that failed in 2020 in the line 18n data? e) Has a root cause analysis been performed on any of the transformers that failed in 2020? If so, please provide the findings of the analysis. f) What are the five most common causes of distribution transformer failures in 2020? g) How many of the 3,405 distribution transformer-related outages from line 18n are in HFTD Tier 2 areas? h) How many of the 3,405 distribution transformer-related outages from line 18n are in HFTD Tier 3 areas? | a) A September 2020 heatwave and the second hottest August (2020) ever recorded (according to National Oceanic and Atmospheric Administration) resulted in an increased number of outages connected to transformers. Specifically, on Labor Day weekend (September 5-7, 2020), over 640 transformers caused outages. Further, in August 2020, SCE experienced almost 400 more transformer failures than compared to August 2019. b) The minimum age of a transformer that failed in 2020 was less than 1 years old per SCE’s system of record. c) The maximum age of a transformer that failed in 2020 was 98 years old per SCE’s system of record. d) The mean age of transformers that failed in 2020 was 37 years per SCE’s system of record. e) The below table contains a summary of the root | 2021-03-10 | 2021-03-15
CalAdvocates-SCE-2021WMP-11 | 002 | Regarding the circuit-level wildfire risk levels that were provided in SCE’s response to Questions 4 and 5 of CalAdvocates-SCE-2021WMP-01. a) Are those wildfire risk levels the current outputs of SCE’s WRRM and Technosylva’s Consequence model? If not, describe which model SCE used to calculate those wildfire risk levels from and which vendor is used to calculate the consequence component of that model. b) If those wildfire risk levels are not the current outputs of SCE’s WRRM and Technosylva’s Consequence model, provide the current circuit-level wildfire risk scores in excel format for all distribution circuits existing in 2020. c) If those wildfire risk levels are not the current outputs of SCE’s WRRM and Technosylva’s Consequence model, provide the current circuit-level wildfire risk scores in excel format for all transmission circuits existing in 2020. | a) The wildfire risk levels mentioned in CalAdvocates-SCE-2021WMP-01 are the current outputs of the WRRM and Technosylva’s consequence model is a part of the WRRM. b) See response to part a) c) See response to part a) | 2021-03-10 | 2021-03-15
CalAdvocates-SCE-2021WMP-12 | 001 | State the total sum of miles of overhead covered conductor that SCE plans to complete in 2021. Use the same project selection criteria that SCE used in response to CalAdvocates-SCE-2021WMP-09, Question 1.a (in which SCE included covered conductor work scope that has completion dates in 2022), except this time applied to your entire service territory. We do not need a detailed list of projects or circuits; only the total number of miles. | Subject to resource constraints and operational restrictions, SCE expects to install 1,000 circuit miles of covered conductor in 2021 but will strive to install as many as 1,400 circuit miles. | 2021-03-12 | 2021-03-16
CalAdvocates-SCE-2021WMP-12 | 001 Supplemental | State the total sum of miles of overhead covered conductor that SCE plans to complete in 2021. Use the same project selection criteria that SCE used in response to CalAdvocates-SCE-2021WMP-09, Question 1.a (in which SCE included covered conductor work scope that has completion dates in 2022), except this time applied to your entire service territory. We do not need a detailed list of projects or circuits; only the total number of miles. | SCE’s original response provided its 2021 WMP Update 2021 target for covered conductor to install 1,000 circuit miles and up to 1,400 circuit miles. SCE’s targets take into consideration operational conditions, as described in SCE’s response to CalAdvocates-SCE-2021WMP-07, Question 2 (and repeated below). To be responsive to the statement “Basically, I'm looking for a ratio here: 1156/xxxx miles of projects are expected to occur on the circuits that we identified in DR 09 question 1. We need the denominator” in your follow up email on March 16, 2021, SCE responds below. For clarity, SCE believes the referenced response is in error and should be DR Set CalAdvocates-SCE-2021WMP-07, Question 1a. Additionally, the referenced 1,156 circuit miles is in error and should be approximately 1,116 circuit miles as included in the attachment to SCE’s response to Question 1a. Furthermore, for the calculation that Cal Advocates is looking to perform, it seems the numerator should not be 1,116 and instead should be 530 circuit miles when considering only the circuit miles that are expected to complete in 2021. The denominator should be either the target 1,000 circuit miles or stretch 1,400 circuit miles provided in response to data request CalAdvocates-SCE-2021WMP-12. SCE further explains below. SCE is providing an updated Excel file similar to the Excel file it provided in its response to Question 1a which only includes circuit miles that have been or will be released to construction and have a projected completion date in 2021 per Cal Advocates selected circuits. In the original response to Question 1a, SCE provided its covered conductor scope of work on the pre-selected circuits expected to take place over multiple years (2020-2022) which amounted to approximately 1,116 circuit miles. In response to Question 2, SCE provided its covered conductor scope of work that has been or will be released to construction and has a projected completion date in 2021. This response included approximately 1,883 circuit miles of covered conductor. SCE’s updated Excel file is a subset of the 1,883 circuit miles as it includes only those circuit miles planned to be completed in 2021 on the pre-selected circuits and excludes those projects that are already experiencing operational challenges. As such, these figures are more comparable than the 1,116 circuit miles included in the original response to Question 1a which included circuit miles planned to be completed over multiple years. Importantly, SCE has scoped a larger volume of work to be completed in 2021 (approximately 1,883 circuit miles) to ensure an adequate number of projects are made available due to operational conditions that may restrict completion of work. Such conditions include site accessibility, weather conditions, customer outage restrictions, environmental restrictions, permits, and agency constraints. Unexpected delays in the design, permitting, and construction processes may also result in projects being deferred. In anticipation of these constraints, SCE needs to scope a larger volume of work to ensure it can meet its compliance target of 1,000 circuit miles and up to 1,400 circuit miles. It’s also important to note that covered conductor work can span many months; however, portions of the work scopes can be completed in shorter durations. | 2021-03-12 | 2021-03-17
TURN-SCE-005 | 001 | 1. Re WMP p. 212: a. Please provide in Excel the list of circuit segments ranked according to risk using the 2019 WRRM model, including at a minimum circuit name, identification, mileage, and relevant risk score. b. Please provide in Excel the list of circuit segments ranked using the new WRRM model (with Technosylva consequence scores), including at a minimum circuit name, identification, mileage, and risk score. | In 2019, SCE used the Wildfire Risk Model (WRM). In late 2020, SCE started its Wildfire Risk Reduction Model (WRRM) risk framework. SCE provides its WRM 2019 model with REAX Engineering consequence scores for circuit segments. SCE also provides the WRRM 2020 model with Technosylva consequence scores (acres multiplied by buildings) for circuit segments. Please see the attached Excel file entitled “wrm2019_wrrm2020_CONFIDENTIAL.xlsx” for the information requested in parts (a) and (b) of this question. The sheets have differing number of segments because the dataset is constantly being refined and refreshed to reflect current grid and circuit connectivity and conditions. The WRM2019 tab is the latest version, which has the best representation of our grid. CONFIDENTIAL The Attachment(s) Are Marked Confidential In Accordance With D. 16-08-024 and D. 17-09-023. Basis for Confidentiality In Accompanying Confidentiality Declaration. Public Disclosure Restricted. | 2021-03-10 | 2021-03-15
TURN-SCE-005 | 002 | 2. Re. WMP, Initiative 7.3.4.9.1: a. Please identify in 2020 how many poles were i) repaired and ii) replaced as part of the remediation work. b. Please identify how much (capital and/or expense) was spent on pole remediations in 2020, disaggregated by repair and replacement if possible. | a) Per SCE’s system of record, SCE completed 3,543 pole replacements notifications and 11,065 repair notifications in 2020 in connection with inspections described in 7.3.4.9.1. b) SCE bundles repair work together, such as those from Inspection activities in 7.3.4.9.1 and other work to achieve operational efficiencies, and therefore cannot break out recorded costs without conducting a detailed study. | 2021-03-10 | 2021-03-15
TURN-SCE-005 | 003 | 3. Re. WMP, p. 215. SCE describes several programs (FRP, PLP, DPP) that replace wood poles. Please provide a spreadsheet that shows for 2019 and 2020 (in Excel) the number of poles replaced, and the total cost of replacement, for each of the main pole replacement programs. | Please note the Fire-Resistant Pole program does not proactively replace poles, when a pole is being replaced in a High Fire Risk Area, such as for the Pole Loading Program, the pole is replaced with a fire-resistant pole. The table below contains the poles replaced under the Pole Loading Program and the Deteriorated Pole Program and the costs associated with those programs. | 2021-03-10 | 2021-03-15
TURN-SCE-005 | 004 | 4. Re. WMP, Table 12, Initiative 7.3.3.6. For each year 2020-2022, please disaggregate the units (# of pole remediations) into i) poles replaced and ii) poles reinforced. | Per SCE’s system of record, there are 286 and 58 distribution pole repairs in 2021 and 2022 in High Fire Risk Areas, respectively. The remaining poles listed in Table 12, 7.3.3.6 would be pole replacements. | 2021-03-10 | 2021-03-15
TURN-SCE-006 | 001 | Please explain and provide all supporting calculations for why SCE chose 4,000 miles as the appropriate target for covered conductor installation by 2022. | SCE stated in its WMP that by the end of 2022, SCE expects to replace over 4,000 circuit miles in its HFRA,1 subject to resource constraints and other execution risks. First, as explained in SCE’s 2021 General Rate Case – Exhibit SCE-15, Vol. 05, SCE’s proposed scope is a subset of the miles of overhead conductor in High Fire Threat Districts that the Commission undertook significant effort to identify as areas of extreme and elevated wildfire risk. Second, when determining the scope of covered conductor, SCE primarily took into consideration the absolute risk reduction, which is the number of structures and acres that could be prevented from destruction as seen in Table II-7 of SCE-15, Vol. 05. Third, SCE’s proposal accounts for the operational realities of deploying covered conductor, which include planning and execution lead time, construction methods, work management efficiencies, and compliance requirements. In considering these factors as well as resource constraints, SCE expects to complete over 4,000 circuit miles by 2022. | 2021-03-12 | 2021-03-16
TURN-SCE-006 | 002 | If SCE does not install covered conductor on a given circuit in the HFRA, will there be no other risk mitigation measures in place on that circuit? If the answer is no, please identify other mitigation measures that SCE will deploy on that circuit. | To adequately address wildfire risk, it is often necessary to deploy multiple mitigation measures on a given circuit whether or not covered conductor is installed. For circuits or circuit segments that are not in scope for covered conductor, other wildfire mitigation measures are still applicable, including, for example, fast-curve settings at remote automatic reclosers (RARs), circuit breakers (CBs), current limiting fuses, and insulated line spacers. In addition, on circuits that either have covered conductor installed or not, SCE will continue to perform inspections, repair equipment as necessary, follow recommended and required vegetation management practices, etc. SCE’s other applicable wildfire mitigations are discussed in the WMPs. | 2021-03-12 | 2021-03-17
TURN-SCE-006 | 003 | Please provide the amount of risk reduction (percent) from the deployment of these 4,000 miles of covered conductor and all other mitigations deployed on these miles. Please provide all supporting workpapers. | See SCE’s response to TURN-SCE-006, Question 004 for the risk reduction based on covered conductor. SCE deploys mitigations on circuits based on risk-informed programs. These can, but do not necessarily, target the same miles that covered conductor will target. SCE does not have the requested risk analysis related to other future mitigations deployed on those same circuit miles as covered conductor. | 2021-03-12 | 2021-03-17
TURN-SCE-006 | 004 | Please provide the amount of risk reduction (percent) from just the deployment of the 4,000 miles of covered conductor. Please provide all supporting workpapers. | SCE assumes the 4,000 miles of covered conductor was derived from Table 12 in the Q4 2020 Quarterly Data Report using the 2020-2022 recorded/forecast period. Over the three‐year WMP period (2020-2022), SCE expects covered conductor to reduce approximately 64% of HFRA wildfire risk. This risk reduction is modelled using SCE’s Technosylva consequences (acres multiplied by buildings) and assumes identified scope will be designed and constructed as modelled. This percentage applies the mitigation effectiveness of covered conductor in the estimate. CONFIDENTIAL PROTECTED MATERIAL The Attachment is Marked Confidential In Accordance With D. 16-08-024 and D.17-09-023 and Non-Disclosure Agreement Basis for Confidentiality In Accompanying Confidentiality Declaration. Public Disclosure Restricted. | 2021-03-12 | 2021-03-17
TURN-SCE-006 | 005 | Please identify whether enhanced vegetation management will also be required on miles where covered conductor is deployed. If the answer is yes, please quantify the cost of enhanced vegetation management on miles where covered conductor is deployed. | SCE objects to the question as vague and ambiguous as to the term “enhanced vegetation management” and interprets that term to mean both SCE’s expanded 12-foot clearance at time of trim program in HFRA as well as SCE’s Hazard Tree Management Program (HTMP) in HFRA. Subject to that objection, SCE responds as follows: It is appropriate to conduct enhanced vegetation management on areas that also have or will have covered conductor deployed for two principal reasons. First, the installation of covered conductor in large quantities takes material amounts of time and wildfire risk needs to be mitigated immediately and in the near-term. Enhanced vegetation management is relatively expeditious compared to the installation of covered conductor. Second, while covered conductor is an effective mitigation against certain wildfire risk drivers, especially intermittent contact from object such as small tree branches, palm fronds, etc., it does not completely mitigate against all types of wildfire risk, including certain vegetation contact blow-ins and fall-ins from large diameter tree trunks and limbs, that SCE’s enhanced vegetation management programs are intended to address. SCE does not track vegetation management costs on a per mile basis and therefore cannot provide the cost for the miles where covered conductor has been or will be deployed without conducting a detailed study. Pruning costs in locations with covered conductor are expected to remain consistent with recently recorded costs. For hazard tree removal, the cost depends on the type, size, location, density and number of trees assessed that require removal which are adjacent to circuits with covered. SCE also does not track these costs by mile and therefore cannot provide the cost for the miles where covered conductor has been or will be deployed without conducting a detailed study. | 2021-03-12 | 2021-03-17
TURN-SCE-006 | 006 | Does the cost of the covered conductor program included in the WMP rely on the same unit costs for installation of covered conductor as the utility used to develop SCE’s 2021 General Rate Case request in A.19-08-013. | The unit cost used in the 2021 WMP is not the same as the unit cost in SCE’s 2021 GRC request. The estimated per unit cost in the 2021 GRC (in constant 2020 dollars) is $462k per circuit mile. The estimated per unit cost in the 2021 WMP Update (in constant 2020 dollars) is $538k per circuit mile. At the time the 2021 GRC forecast was developed, SCE had completed a limited amount of covered conductor and therefore used unit costs from a similar conductor replacement program (SCE’s Overhead Conductor Program) and added costs for the requirements for covered conductor. Since SCE has completed a substantial amount of covered conductor, the 2021 WMP unit costs were updated with recorded actual unit costs for covered conductor work. Additionally, the covered conductor program unit costs in the 2021 WMP included Fire Resistant Poles, whereas those costs were accounted for separately in SCE’s 2021 GRC unit costs. | 2021-03-12 | 2021-03-16
TURN-SCE-006 | 007 | Table 3-2 on pages 30-31 of SCE’s WMP shows a difference of $379,259 for planned versus actual expenditures in 2020. Please provide all reasons for the lower actual spend than planned. | SCE objects to this question as costs and cost recovery are outside the scope of the Wildfire Mitigation Plans pursuant to California Public Utilities Code Section 8386.4.(b)(1). Notwithstanding this objection, SCE provides comments in the attached Excel file for System Hardening 2020 reconciliation of all sub-activities. | 2021-03-12 | 2021-03-17
TURN-SCE-007 | 001 | At Page 65 of its WMP, SCE references a “risk curve.” a. Please provide the referenced risk curve and all supporting workpapers. b. Please specify if this is the same risk curve relied on by SCE in its 2021 General Rate Case filing. c. If the answer to subsection b is no, please explain any differences. | a) The risk curve is provided below. Attached are the workpapers that support the risk curve.The horizontal axis in the figure represents the cumulative circuit mileage in the HFRA, and the vertical axis represents the sum of all the wildfire risk in terms of both probability of ignition and consequences for circuit segments in HFRA. b) We object to this question on the grounds that information regarding the GRC and cost recoveryis outside the scope of this proceeding. Notwithstanding this objection, we respond as follows: No, this is not the same risk curve that SCE included in its 2021 GRC Filing. c) For the 2021 WMP, SCE developed a risk curve using an updated methodology at the circuit-segment level, as described in the WMP. The results in the figure above show that the risk is not uniform and that some segments exhibit significantly more wildfire risk than others. In addition, the risk associated with each circuit may not be uniform along its length, i.e., the risk can vary extensively between a specific mile or segment within a circuit. This is especially true if that circuit traverses various tiers and is exposed to different probabilities of ignition by contact from objects, or varying topography and vegetation that can influence fire propagation and consequence. CONFIDENTIAL The Attachment(s) Are Marked Confidential In Accordance With D. 16-08-024 and D. 17-09-023. Basis for Confidentiality In Accompanying Confidentiality Declaration. Public Disclosure Restricted. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 001 | SCE did not provide any of the following information in its Q4 GIS data submission. The data status tracker indicates that each was submitted. Provide the following or explain why it is not available: 1(a). “PSPS Customer Meter Point” data 1(b). “Transmission VM outage” data 1(c). “PSPS event conductor damage detail” table 1(d). “PSPS event support structure damage detail” table | SCE makes every effort to provide the best quality data at a specific point in time to meet the WSD GIS Data Quarterly Deliverable. The second Quarterly Report GIS data submission (12/9/20) was SCE’s second time submitting the GIS data so there were still many data fields that may have resulted in a blank field or we were unable to modify our Extract, Transfer, & Load (ETL) process quickly enough to provide in the geodatabase. “PSPS Customer Meter Point” table data was collected, but SCE was not able to successfully process that data in time to include in the geodatabase. SCE does intend to submit this data as part of the Q1 2021 Quarterly Data Report submittal due on May 1, 2021. Both the “PSPS event conductor damage detail” and “PSPS event support structure damage detail” tables were left blank as no information was identified related to the PSPS damage data at the time of report development for the period in question. Lastly, the “Transmission VM Outage” data table was left blank due to no known Transmission VM related outages for the period in question. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 002 | Regarding the dataset SCE used for the 2021 Wildfire Risk Model: 2(a). Confirm that SCE utilized outage data as a proxy for ignition data to train the model as stated at the 2/22/21 workshop. If this is not correct, explain what dataset was utilized. 2(b). How many years of outage data did SCE use to train the model? 2(c). How many years of outage data did SCE use to test to model? 2(d). How many events did SCE utilize to train the model? 2(e). How many events did SCE utilize to test the model? 2(f). For outage data used by SCE, was it possible for SCE to determine the exact location of the issue leading to an outage for each outage event? If it was not possible, did SCE utilize the outage event as part of the training dataset? | a) Not all outages can lead to sparks. For example, many outages are due to factors such as underground, source loss, and de-energization for upstream repair. Furthermore, not all spark-causing outages lead to ignitions as ignitions may depend on the presence of other factors such as weather and fuels. The probability of ignition model is therefore the combined probability of two outcomes: the likelihood that an outage leads to a spark and the likelihood that a spark leads to a fire. Outage data is used to model the likelihood that an outage at a specific piece of equipment will cause a spark, and historical fire data is used to model the frequency that a spark from a given piece of equipment leads to a fire. Saying “outage data is a proxy for ignition” is only encompassing half of the failure picture that is modeled. b) Ten years of outage data is used to train the model. c) A fraction of randomly sampled events from the ten-year data is held for testing. Furthermore, an additional year, distinct from the train/test decade, is withheld to validate the accuracy over time. d) Roughly 54,000 events are used to train the model. e) Roughly 23,000 events are used to test the model. f) The precise location is associated with the affected structure, which is identifiable for a majority of outages used in building the model. Outages without a location recorded and whose causes are those of interest for modeling are still included in the model building. The probability of failure is associated with each possible structure based on outage notes, nearest protection device, or circuit affected. No outage that could lead to a spark is omitted from the model building. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 003 | Regarding SCE’s decision to utilize outage data versus ignition data in its 2021 Wildfire Risk Model: 3(a). Why did SCE choose to utilize outage data versus ignition data? 3(b). Describe any issues SCE encountered with utilizing outage data. | a) SCE would like to clarify that both outages and ignitions are used. Outages are modeled in order to provide probabilities that a failure event would happen; however, not all events lead to an ignition. Because of this, any fault that could lead to an ignition is modeled, and each probability is further calibrated to the number of expected fires based on the ignition data. b) As described in SCE’s response to question 2(f) of this data request set, SCE encountered some challenges with outage data relating to identifying the exact location of certain outage events. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 004 | At the 2/22/21 workshop, the Energy IOUs indicated that for the Consequence Model, Technosylva provides options for using maximum, average, or 90% (P90) values for consequences for wind speed. SCE indicated in the workshop that for planning and mitigation work, it “likely” uses the maximum consequence. 4(a). Does SCE always use the maximum consequence for planning and mitigation work? If SCE does not always utilize the maximum consequence for planning and mitigation work, explain the circumstances and reasons for using other levels of consequence. 4(c). How are the various aspects of the “consequence” weighted? Is the weighting determined by Technosylva or by SCE? 4(d). Does SCE always use the maximum wind speed in the Technosylva Consequence Model? If SCE does not always utilize maximum wind speed in the Technosylva Consequence Model, explain the circumstances and reasons for using a different wind speed. | (a) SCE did not calculate RSEs for the activities and programs in the table below. Please see response to the previous question. (b) The initiatives in Table Q12 either do not have a direct impact on probability and consequence of ignition or de-energization or are not SCE WMP activities, and SCE provided an explanation, in the respective WMP section, as to why an RSE was not calculated. SCE has added an extra column to the table, including page number reference and the description given in SCE’s WMP filing. For the reasons cited below, there is no plan to calculate RSE’s for these initiatives. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 005 | At the 2/22/21 workshop, SCE indicated that for Probability of Ignition (POI) Models, SCE uses “outages that can lead to a spark” and “all outages”. 5(a). How do the POI models use the “outages that can lead to a spark” data? 5(b). How do the POI models utilize the “all outages” data? 5(c). How does SCE determine what outages can lead to a spark? | a) As with a linear or logistic regression model, there are independent or explanatory variables and there are dependent or response variables that the models attempt to generate by finding patterns in the explanatory data. The POI models use outages that lead to a spark as failure targets, i.e., the response variables or the events that we are trying to model. In order to discern between events that we are trying to model and those that we are not, outage data are combined with a random sample of equipment that did not fail. This set of failures and non-failures (classifications) are paired with their various explanatory variables that the asset experienced during the time period. The model then finds decision thresholds in the explanatory data that most accurately separates the failures from the non-failures, while minimizing misclassifications. Furthermore, a subset of these outages is withheld from the model training to test the accuracy of the decision trees built by the algorithms. b) To clarify, all outages are used to create a subset and extract outages that can lead to a spark, based on the cause description and code. c) The full set of outage causes was reviewed with Reliability and Grid Operations groups to isolate causes that could result in arcing or flashovers such as vegetation contact, arcing transformers, and wires down. These outages were separated from those that would not lead to sparks such as source | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 006 | At the 2/22/21 workshop, SCE discussed MARS 2.0. SCE stated that the combined output of the MARS Wildfire Risk Score and the MARS PSPS Risk Score can be used to show where it’s best to deploy mitigation options. 6(a). Are these risk scores provided at the circuit segment level? 6(b). Did SCE utilize the MARS PSPS Risk Scores to determine where to deploy mitigation options? If so, how were the PSPS Risk Scores used and weighted compared to the Wildfire Risk Score? If not, when does SCE expect to begin utilizing these scores? 6(c). Did SCE utilize the MARS PSPS Risk Scores in selecting which mitigation options to utilize for each circuit segment? If so, how were the risk scores used? If not, when does SCE expect to begin utilizing these risk scores? 6(d). Did SCE utilize the MARS Wildfire Risk Scores to determine where to deploy mitigation options? If so, how were these risk scores used? | a. Yes. b. No. SCE anticipates it will begin to use this methodology for mitigations deployed in 2023. c. No. SCE anticipates it will begin to use this methodology for mitigations deployed in 2023. d. No. SCE previously used the product of probability of ignition and Reax consequence. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 007 | Regarding SCE’s switch from REAX to Technosylva: 7(a). How did switching consequence modeling change the risk ranking of circuit segments? 7(b). How did switching consequence modeling change the prioritization of system hardening projects? 7(c). What percentage of previously identified top 25% riskiest circuit segments were also identified within the top 25% by the Technosylva model? 7(d). What percentage of previously identified top 10% riskiest circuit segments were also identified within the top 10% by the Technosylva model? 7(e). What were the leading causes of any shifts described in (c) and (d)? 7(f). How is consequence risk weighed against ignition risk when utilizing Tehnosylva? | a) Technosylva utilizes more recently updated input data, namely population, building, and available burnable fuel. This changed the risk ranking to better reflect the current consequences, which resulted in some segments moving up in rank and some moving down versus REAX. b) With the implementation of Technosylva, any segments that were considered high risk by Technosylva, but were not previously identified as high risk by REAX, were brought into the current scoping tranche. In-flight work will remain on course; however, SCE is evaluating opportunities to accelerate the new scope where operationally practical. c) 25.8% of the top 25% of ranked circuits according to REAX were identified by Technosylva d) 13.1% of the top 10% of ranked circuits according to REAX were identified by Technosylva e) More recent population, building, and fuel data. f) In situations where both ignition risk and consequence risk are used for decision making, SCE uses a total risk score defined as POI multiplied by consequence score. There are no additional weightings added to these variables. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 008 | SCE states that “[any] segments that ranked higher in the WRRM than the previous risk models and were not already scoped for construction were prioritized for 2022 construction. This method will ensure all the highest risk segments identified in our updated risk model will be completed by the end of 2022.” (WMP p. 212) 8(a). Define what is meant by “highest risk segments” and provide the percentage of such risk segments. 8(b). Provide the total number of circuit segments ranked. 8(c). Provide the total number of circuit segments that ranked higher in the updated model compared to the previous model. 8(d). Does SCE intend to complete construction of the previously ranked segments after the higher risk segments are hardened? Why or why not? | 8(a). The highest risk segments identified by WRRM for covered conductor were segments with risk scores between 22.5 and 15,720 (acres times buildings) using the Technosylva model consequences. This reflects 2.9% of all SCE system circuit segments and 14.7% of all SCE HFRA circuit segments. Rather than use a specified percentage cutoff to determine “highest risk segments,” SCE identifies the segments for deployment each year based on consideration of segment risk, business unit needs, and approved project scope. 8(b). The total number of circuit segments ranked is 703,193 circuit segments. In HFRA, the total number of circuit segments ranked is 139,941. 8(c). The total number of circuit segments that ranked higher in the updated model compared to the previous model is 155,071 circuit segments. In HFRA, the total number of circuit segments that ranked higher in the updated model compared with the previous model is 66,355. SCE intends to complete construction based on the risk-informed scope of segments as previously ranked, from highest to lowest. However, operational challenges and efficiencies (e.g., permitting delays, opportunities to combine work in a single project, resource constraints) can result in reprioritization in some cases. 8(d). No, SCE will not necessarily complete construction of the previously ranked segments after the higher risk segments are hardened, due to the necessity of completing work already in the project pipeline. The pipeline contains work orders that were developed based on the prior model that are still in the HFRA; these work orders address both higher and lower risk segments. SCE intends to complete all work orders in the pipeline, because of the time it takes to create new work orders and SCE’s preference to complete relatively lower risk projects that still provide meaningful risk reduction (rather than do nothing) while waiting to add higher risk projects to the pipeline. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 009 | In SCE’s 2/22/21 workshop presentation, a footnote indicated “2021 scope may be based on prior risk models” for system hardening projects. 9(a). What percentage of the 2021 scope is based on prior risk models? 9(b). What percentage of the 2021 scope is based on the Technosylva risk model? 9(c). What percentage of the prior risk model scope was also identified by the Technosylva model for prioritization? 9(d). What percentage of the projects identified with prior risk models were cancelled as a result to changing model output? | SCE answers this question based on planning year 2021, which uses structures as the unit of measurement. 9(a). 100 percent. SCE had projects in the pipeline for 2021 that are based on the prior risk models and has not incorporated Technosylva into those projects. 9(b). 0 percent. SCE had projects in the pipeline for 2021 that are based on the prior risk models and has not incorporated Technosylva into those projects. 9(c). Of the segments based on prior risk models that are associated with in-design, planned, and completed covered conductor scope for 2021, 74% have Technosylva risk scores that are high enough to have been targeted by the latest round of scope proposed for covered conductor using Technosylva (acres times buildings) consequences. Similarly, Technosylva would have accounted for 74% of the miles based on the prior risk models associated with the 2021 scope. 9(d). 0 percent. SCE has not canceled any prior projects as a result of changing model output. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 010 | Provide a list that ranks all wildfire risks or point to where it is in the Wildfire Mitigation Plan. | SCE interprets this question to request a ranking of risk drivers from highest to lowest risk. Below are the drivers ranked from highest to lowest ignition rates. Drivers without ignitions have been left out for clarity. This analysis does not consider consequences of ignitions. Category is the major category – Equipment Facility Failure (EFF) or Contact from Foreign Object (CFO), for Transmission (T) or Distribution (D). Sub-cause category is the reason for the outage. Average Outage is the average number of outages per year from 2015 through 2020. Ignition Rate is the average Rate of Ignitions per year calculated from 2015 through 2020. Adjusted Risk is the product of Average Outage * Ignition Rate. Ignition Rank is the ranking of adjusted risk | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 011 | For Capability 41a of the 2021 Maturity Survey, SCE selected “Accurate RSE estimates for all initiatives are used to determine capital allocation within categories only (e.g., to choose the best vegetation management initiative)” for the year 2021. In Table 12 of its WMP, SCE reported 11 initiatives that have positive capital costs but no RSE estimations. These initiatives are listed below in Table Q11. For each initiative in Table Q11: 11(a). Provide the RSE values for the 11 initiatives that contribute to capital costs. 11(b). For each initiative that (a) cannot be completed, identify the missing variables necessary to complete the RSE calculations, detail the plan to obtain the necessary variables, and the timeline for completion. | (a) SCE did not calculate RSEs for the WMP activities and non-WMP programs in the table provided. Please see response to question (b) below. As discussed in Chapter 4 of SCE’s 2021 WMP Update, SCE calculates wildfire risk based RSEs and uses risk analysis to assess all WMP activities and drive work prioritization for (1) activities which were initiated to mitigate wildfire risks and (2) which are expected to directly reduce probability or consequence of ignitions. WSD required discussion of several utility programs that SCE did not initiate to mitigate wildfire risks. SCE has performed these programs prior to the initiation of WMP submittals, and though they may have some wildfire mitigation benefits, wildfire mitigation was not the primary driver to undertake these programs. Therefore, SCE does not categorize these as WMP activities and have not systematically completed RSE calculations for these programs. In addition, there are WMP activities that are foundational or supporting activities, such as technology projects, which by themselves do not reduce wildfire risks. However, they help other activities to deliver the expected RSE. Calculating RSEs for these would be speculative at best and un-informative. Calculating RSE’s for activities that are “enabling” or have indirect impacts are not meaningful as these activities do not target specific risk drivers (e.g. Contact from Object-Animal, etc.) – this is a specific requirement in order to calculate an effective RSE. Additionally, in SCE’s Maturity Survey Response Overview (submitted in last year’s 2020-2022 WMP), SCE further clarified that though RSE calculations are an important input into the capital allocation process, SCE considers other inputs as well such as certain operational realities, resource constraints, work management efficiencies and other regulatory compliance that must be considered as part of its plan. For example, SCE might undertake an activity even if it has low RSE as it is a relatively low-cost alternative that addresses a specific risk driver that needs to be mitigated. Accordingly, SCE calculated RSEs for those activities that have a direct impact on probability and consequence of ignition or de-energization or are SCE WMP activities. SCE has added an extra column to the table provided by the WSD, including page number reference and the description given in SCE’s 2021 WMP Update filing. For the reasons discussed above, there is no plan to calculate RSEs for these initiatives. | 2021-03-12 | 2021-03-16
WSD-SCE-004 | 012 | In addition to the initiative outlined in the question above, SCE did not provide RSE values for many initiatives that have a direct impact on the probability and consequence of ignition or de-energization. For each initiative in Table Q12: 12(a). Provide RSE values. 12(b). For each initiative that (a) cannot be completed, identify the missing variables necessary to complete the RSE calculation, detail the plan to obtain the necessary variables, and the timeline for completion. | (a) SCE did not calculate RSEs for the activities and programs in the table below. Please see response to the previous question. (b) The initiatives in Table Q12 either do not have a direct impact on probability and consequence of ignition or de-energization or are not SCE WMP activities, and SCE provided an explanation, in the respective WMP section, as to why an RSE was not calculated. SCE has added an extra column to the table, including page number reference and the description given in SCE’s WMP filing. For the reasons cited below, there is no plan to calculate RSE’s for these initiatives. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 013 | In the 2021 WMP submitted 2/5/2021, SCE reported 12 PSPS events for 2020 when summing rows 1.a. (events with de-energization) and 5.a. (events with no de-energization) in Table 11 of “SCE Tables 1-12.xlsx". SCE filed 12 PSPS after-action reports for 2020, but two reports included multiple events. (Definition of a PSPS event from the WMP Guidelines: The time period from the first from the first public safety partner notified of a planned public safety de-energization to the final customer re-energized.) SCE’s PSPS after action reports submitted for Dec. 7 – 13 and Dec 18 – 25 consolidated 3 and 2 PSPS events respectively. Including an additional event from Dec 15 – 16 where no customers were de-energized and no after-action report was filed, SCE had 16 PSPS events in 2020. Confirm rows 1.a. and 5.a. in Table 11 below, now totaling 16 PSPS events in 2020: | Pursuant to the CPUC’s PSPS guidelines, including Resolution ESRB-8, D.19-05-042, and D.20- 05-051, SCE filed 12 PSPS post event reports encompassing 16 periods of concern for potential fire-risk weather in 2020. SCE defines periods of concern as times of elevated or extreme fire weather that could result in de-energization. There may be more than one period of concern reflected in an SCE post event report if periods of concern are forecasted concurrently within one PSPS event. Periods of concern may also result in customers being notified of the potential for deenergization with no de-energization occurring based on actual weather at the time of concern. As noted, two of the periods of concern in SCE’s post event reports resulted in no de-energizations. Accordingly, SCE believes that no adjustment needs to be made to the referenced parts of SCE’s Table 11. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 014 a | SCE states (p. 188): “As the WRRM is now implemented, SCE will no longer list RA-1 as a WMP Activity.” 14(a). If it is no longer a WMP activity, what is RA-1 now considered? | RA-1, which represented the implementation of WRRM, is now considered completed, as SCE has implemented the WRRM. | 2021-03-12 | 2021-03-16
WSD-SCE-004 | 014 b-d | SCE states (p. 188): “As the WRRM is now implemented, SCE will no longer list RA-1 as a WMP Activity.” 14(b). Where will improvements and maintenance to the system/process be accounted for? 14(c). RA-1 does not appear in Table 12. Is RA-1 accounted for under SA-4 in 2021 WMP Table 12? 14(d). RA-1 and SA-4 appear together in 2020 WMP Table 22. In the 2020 WMP, the expected cost was estimated to be $6,682,000 in capital costs, in the 2021 WMP, the actual was recorded as $1,029,000 in operational costs. Was this money reallocated? What accounts for the change from capital to operational costs? | 14(b). In the 2021 WMP, SCE included the annual licensing costs of the WRRM in Initiatives SA-3 and SA-4. The annual licensing costs were included in these two initiatives because RA-1 was completed and these two initiatives also support WRRM usage. Pursuant to a previous WSD request, SCE allocated a portion of these costs to the Risk Assessment and Mapping category within 7.3.1.1, 7.3.1.3, and 7.3.1.5 (Please also see the attached Excel file). Going forward, these annual licensing costs will be reported in the relevant Risk Assessment and Mapping section. The other Fire Science and Advanced modeling sub activities will be captured within Situational Awareness under their related Initiative similar to 2021. 14(c). RA-1 was not an activity in the 2021 WMP as implementation was completed in 2020. 14(d). Please note that the $6.682 million is incorrect. The correct amount is $6.692 million as reported in the 2020 WMP. Additionally, the referenced $1.029M is O&M costs but for a different activity. The 2020 WMP costs previously captured in RA-1 are now grouped with sub-activities in SA-3 and SA-4.1 SCE is providing a table (below) with cost details and a description to explain the $6.692 million and the $1.029M and their correlation from the 2020 WMP to the 2021 WMP Update. The 2020 estimated costs were $6.692M in Capital.2 This forecast consisted of 2 activities: Asset Risk Modeling (ARRA) Technology Solution was forecast at $3.9M3 • The program recorded $3.8M in 2020. As seen in the table below, SCE included $1.5M for 2020 recorded (See the second number 2 reference in the table). SCE inadvertently under reported an additional $2.3M due to accounting. This will be revised in subsequent WMP and Table revisions to show a total of $3.8M for 2020 recorded for this technology solution.4 • Operational Analytics Technology Solution was forecast at $2.7M5 • The program recorded $.27M in 2020.6 o The 2020 estimate was a conceptual estimate given that the vendors and solution were not finalized at the time of the 2020 WMP filing. The 2020 recorded spending underrun was due to SCE completing the original scope of work under forecast. This 2020 recorded amount is included in the number 3 reference in the table below. oIn the 2021 WMP, SCE added incremental scope of work to procure two additional super computers which were not reflected in the 2020 WMP. The 2021 forecast of $1.5M and the 2022 forecast of $700K included in the 2021 WMP are to support the new super computers which are needed to provide a 1 km resolution, rather than a 2 km resolution, to support the configuration, installation, and new integration with the wildfire risk modeling. The $1.029M recorded amount is related to a separate O&M activity entitled "Surface and Canopy Fuels Mapping," not to be confused with the two unrelated capital activities referenced above. The 2020 WMP forecast for this activity was $1.38M.7 See reference number 4 in the table below. There was no reallocation of costs. The question posed is mixing capital activities in SA-38 with Operational activities in SA-4.9 The activities and associated costs in SA-3 and SA-4 are unrelated to each other. There was also no change from Capital to Operational costs that took place, as noted above. Please see the table below for references and please note the second column references specifying whether activities are Capital or O&M. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 015 | Provide details on how the scope and content of increased asset inspection efforts differ from routine inspections apart from frequency of execution. | Apart from frequency of execution, SCE’s High Fire Risk Informed Inspections differ from traditional routine inspections in two key ways: (1) They have a different focus and purpose: inspections go beyond identifying the conditions of existing assets that could be safety or reliability hazards under GO 95, and extend to identifying potential upgrades or other modifications to the assets that would help mitigate ignition risks based on recent data; and (2) They are conducted in different ways: aerial inspections and high-quality image capture provide a 360-degree view of assets that was previously unachievable from the ground inspections alone. The table below provides further information. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 016 | Provide the fire rebuild standards utilized during post-fire repairs and replacements. | Please refer to SCE’s response to WSD-SCE-002, Q1 and the attachments to this data request question. Construction during rebuild of distribution systems, transmission systems, and/or telecommunications systems must follow the following standards, where applicable:  Distribution Design Standard (DDS) for distribution voltages 33 kV and below  Distribution Overhead Construction Standard (DOH) for distribution voltages 33 kV and below  Transmission Overhead Construction Standards (TOH) for transmission lines voltages of 66 and 115 kV  Standard Specification – Transmission No. SST3-2017 (SST3) for transmission line voltages of 220 kV and above  Transmission Telecommunications Construction Standards (TTCS)  Transmission Telecommunications Planning and Design Manual (TTPD) CONFIDENTIAL The Attachment(s) Are Marked Confidential In Accordance With D. 16-08-024 and D.17-09-023. Basis for Confidentiality In Accompanying Confidentiality Declaration. Public Disclosure Restricted. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 017 | What percentage of hazards identified by machine learning were not captured by inspectors previously? | In 2020, SCE’s aerial inspection program piloted a machine learning model to detect deteriorated cross arms. The machine learning model was trained on defects identified by human inspectors. The machine learning model was validated by the aerial inspection program inspectors. The model correctly identified an additional 1.72% of the hazards beyond what the inspectors identified. Because the model also incorrectly identified potential hazards, the model is currently used in an advisory mode meaning when the model detects a defect, the structure is prioritized for a human inspector to review. | 2021-03-12 | 2021-03-16
WSD-SCE-004 | 018 | What threshold(s) are being utilized for spacer installation based on LiDAR data to prevent conductor clashing? | Line spacers, for the purpose of mitigating conductor clashing, are installed on horizontal spans (crossarm construction) when the sag of adjacent conductors is equal to or greater than the horizontal separation between said conductors. The horizontal separation of adjacent conductors is captured via LiDAR either at the insulators or along the span, whichever is smaller. The diagram below provides an illustrative example. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 019 | When does SCE intend to complete analysis on determination of raising wind thresholds for PSPS events based on installation of covered conductor and other system hardening efforts? | There is no one point in time for completing this work because the process to determine whether circuits or circuit-segments that have been covered are fully hardened is a continuous effort. When an isolatable circuit or circuit-segment has been fully covered, SCE adjusts its PSPS algorithm to reflect the current methodology of using the National Weather Service’s High Wind Warning criteria. This adjustment occurs each time a new segment or entire circuit is confirmed to have been fully hardened with covered conductor and will be ongoing as more segments and circuits are covered in the future. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 020 | Breakdown the cost increase for covered conductor installation, given that SCE's total scope has not changed since 2020 WMP to apply to HFRAs. | The cost increase in Covered Conductor (SH-1) between the 2020 WMP vs 2021 WMP (2020-2022) is $301M. The 2020 WMP 3 year total is $1,883M and the 2021 WMP 3 year total is $2,184M. This variance is driven primarily by two reasons: • The 2020 WMP did not include Fire Resistant Poles within SH-1. In the 2020 WMP, Fire Resistant Poles was a standalone item (SH-3) and the total costs from 2020 through 2022 for SH-3 equaled $194M. In the 2021 WMP, Fire Resistant Poles is included within the SH-1 category. As such, the costs for covered conductor (SH-1) in the 2021 WMP included the $194M for SH-3. • In 2018, SCE built a bottoms-up covered conductor unit cost forecast using its Overhead Conductor Program (OCP) as a basis. This unit cost was used in the 2020 WMP (escalated as appropriate with time). For the 2021 WMP, SCE was able to update estimates using a recorded actual unit cost for covered conductor work. Increases between the two estimates were driven primarily by an ~20% increase in electrical crew contracted rates, due to local market conditions. Additionally, to meet execution requirements, SCE increased contractor utilization in the design and planning phase by 18%. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 021 | In its response to Data Request 003, SCE provided excel Table “WSD-SCE-003-002_20210309” in which spending is categorized in Column “V” as “WMP activities” and “Non-WMP programs.” 21(a). Define “WMP activities” 21(b). Define “Non-WMP programs” 21(c). What is SCE’s criteria to differentiate the two types of spending categories? 21(d). Is anything otherwise determining the difference in those two types of spending categories? 21(e). Why are certain initiative activities marked as “new” (column P) and also marked as a “non-WMP” (column V)? | a) SCE considers WMP activities to be activities which are initiated to primarily address wildfire risks and/or PSPS impacts. Most of these have specific program targets and are included in Table 5.3-1 on pp. 104-127 of SCE’s 2021 WMP Update and in the reconciliation Excel file titled “WSD-SCE-003-002_20210309” that was submitted as an attachment to SCE’s response to WSD-011_WSD-003 Q.002. b) SCE considers Non-WMP programs to be programs which are not initiated to primarily address wildfire risks and/or PSPS impacts. These programs are implemented for purposes primarily outside of wildfire / PSPS impact mitigation (e.g., for reliability), though they may provide indirect wildfire / PSPS impact mitigation benefits. Therefore, these programs would continue even if wildfire and/or PSPS risk did not exist. These programs can also include work we are doing as part of standard operations. Discussion on these programs were included in SCE’s 2021 WMP Update because the WSD’s 2021 WMP Guidelines require this information. Notably, in some cases, the primary intent of a program – specifically within SCE’s High Fire Risk Areas (HFRA) – can evolve or expand over time. For example, traditional compliance-driven vegetation management activities have been modified to go beyond regulatory requirements (e.g., CPUC recommended clearance distances in HFRA) to address wildfire risks associated with vegetation. In cases where the activity goes beyond regulatory requirements, SCE considers that wildfire/PSPS-driven portion to be a wildfire activity. In some instances, it is infeasible to separate out the “compliance-driven” or “standard operation” work from the wildfire/PSPS-driven “expanded” work (e.g., vegetation clearances in HFRA and High Fire Risk Informed Inspections), in which SCE considers the full activity in HFRA to be a WMP activity. c) SCE considers the intended purpose and drivers of each program when determining whether it qualifies as a WMP activity or not. If the program was designed to primarily address wildfire/PSPS risks, then SCE classifies it as a WMP activity. For example, SCE identified new wildfire-driven activities in 2018 as part of SCE’s Grid Safety & Resiliency Program (GSRP) Application that were specifically initiated to address wildfire risk. Then, in subsequent WMPs, SCE proposed several additional new WMP activities to specifically address wildfire/PSPS risk. These would all be considered “WMP Activities.” This is contrary to established programs that have been approved by the CPUC for purposes outside of wildfire and PSPS impact mitigations. For example, SCE’s Pole Loading Program (PLP) is primarily a compliance program and not one primarily driven by wildfire risk reduction or one of SCE’s wildfire mitigation initiatives. While PLP improves safety and reliability, which may include avoiding potential wildfire risks associated with pole failures, PLP is not primarily driven by wildfire mitigation, and is therefore considered a non-WMP program. The general criteria SCE used for the 2021 WMP Update is as follows: • An activity initiated to primarily address wildfire risks and/or PSPS impacts and should be wholly or largely contained to the HFRA • The expansion/modification of an activity for which the expansion/modification was initiated to primarily address wildfire risks and/or PSPS impacts and should be wholly or largely contained to the HFRA • Should an existing activity be expanded/modified for which the expansion/modification was initiated to primarily address wildfire risks and/or PSPS impacts and where it is infeasible to separate the normal or compliance work from the expanded/modified work, the entire activity is considered a wildfire activity but only in or largely in the HFRA d) Yes, in previous WMPs, SCE considered other factors such as costs, cost recovery mechanisms, CPUC programs outside of the WMP, and level of scope definition in determining a Wildfire versus non-Wildfire Activity (See SCE’s response to part e) below for examples). For the 2021 WMP Update, SCE updated how it assesses a wildfire versus a non-wildfire initiative. e) In 2020, SCE may have misinterpreted the New/Existing category and/or marked them in error during the compressed timeline to meet the WSD’s new and comprehensive 2020 WMP requirements. At the time, SCE had to make some simplifying assumptions and largely followed the cost recovery mechanism for determining what was new or existing. For example, if the program was included in the 2018 GRC it was marked as existing. Likewise, if the program was identified for a new memorandum account treatment, it was marked as new. In several instances and as noted in the comments field, if a “new” category was embedded in another category, it was identified as non-WMP, and the activity it was included in was marked accordingly . The comments column provides the supporting documentation for these determinations. The majority of Initiative Activities marked as new, but non-WMP, were activities that had no cost forecast in SCE's 2020 WMP and thus were not included as WMP Initiatives. There were four activities that did have costs but were excluded in SCE’s 2020 WMP forecast for the following reasons: (1) Improvement of Inspections was not included as the costs represent efforts beyond those in SCE's WMP; (2) SGIP Resiliency was excluded as it was being funded through a separate mechanism (See D.20-01-021); (3) Centralized repository for data was not included as this was a preliminary estimate and SCE had not defined the requirements specific to wildfire-related needs, however the component related to wildfire is included in SCE's 2021 Update; and (4) The DRI program was excluded in 2020 as it was being funded out of SCE’s Catastrophic Event Memo Account (CEMA) in 2020. For the 2021 WMP Update, SCE made updates to its assessment of WMP vs non-WMP initiatives from its 2020 WMP. For example, although DRI was being recovered through SCE’s CEMA, this initiative, initiated in 2014 as a result of CPUC Resolution ESRB-4, primarily focuses on reducing the likelihood of wildfires. Because this initiative was (and still is) primarily focused on reducing wildfire risk, SCE determined that DRI should be a wildfire initiative and made this change in its 2021 WMP Update. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 022 | Regarding utilization of vibration dampeners for covered conductor: 22(a). What is the per-unit cost for the vibration dampeners being used for covered conductors? 22(b). What is the additional circuit-mile cost for the vibration dampeners being used for covered conductors? 22(c). What is the additional total cost to the covered conductor program due to the implementation of vibration dampeners? 22(d). How does the addition of vibration dampeners affected the RSE value of covered conductor? 22(e). What conditions and circumstances require vibration dampeners as part of the standard for bare conductor? 22(f). What percentage per circuit-mile of bare conductor throughout SCE’s service territory require vibration dampeners? 22(g). What percentage per circuit-mile of bare conductor within HFRAs require vibration dampeners? | a) SCE utilizes two types of vibration dampers for covered conductor: one for smaller diameter conductors and the other for larger diameter conductors. The average per-unit cost of a spiral vibration damper (used for smaller wire) is approximately $65 and the average per-unit cost of a Stockbridge damper (used for larger wire) is approximately $80. b) The projected weighted cost for vibration dampers is $4,100 per circuit mile. The following assumptions were included in this calculation: 1. One damper per phase, per span for the spiral vibration damper and two dampers per phase, per span for the Stockbridge damper. 2. The average span length is 180 ft. 3. Spiral vibration dampers will be used 86% of the time and Stockbridge dampers will be used 14% of the time. This assumption is based on existing covered conductor installations. 4. Vibration dampers will be required in 78% of covered conductor installations. This assumption is based on 78% of HFRA having an elevation of 3,000 ft or less. Per circuit-mile $ = 5,280 ft/mile ÷ 180 ft/span × 2.3 average conductors/span × (86% × $65/spiral + 14% × $80/Stockbridge × 2) × 78% usage = $4,120. c) In 2021, assuming a target of 1,000 circuit miles of covered conductor, the total vibration damper cost is estimated to be approximately $4.1 million. In 2022, assuming a target of 1,600 circuit miles of covered conductor, the total vibration damper cost is estimated to be approximately $6.6 million. d) The addition of vibration dampers may minimally decrease the RSE value of covered conductor due to the incremental cost increase. Vibration dampers mitigate the risk of premature failure of the covered conductor; therefore, the installation of vibration dampers will help ensure that the useful life of the covered conductor, which is taken into account in the covered conductor RSE calculation, is maintained. e) For bare wire, SCE requires the installation of dampers for new construction on spans greater than 300 ft in areas with an elevation of 3,000 ft or less. f) Approximately 90% of distribution overhead circuit miles in SCE’s service territory is located in areas with an elevation of 3,000 ft or less. However, span length information is not available. For new construction of bare wire, dampers will be installed on spans greater than 300 ft. in 90% of SCE’s service territory. g) Approximately 78% of distribution overhead circuit miles in HFRA are located in areas with an elevation of 3,000 ft or less. However, new construction in HFRA will be constructed with covered conductor and not bare wire. | 2021-03-12 | 2021-03-17
WSD-SCE-004 | 023 | How does SCE differentiate ignition risks within its risk modeling efforts and weigh different ignition risks when determining mitigation options? For example, does SCE change inputs based on the risk ranking of an ignition source (such as weighing vehicle or balloon contacts more heavily), or change inputs based on the probability of an ignition source occurring under particular climate conditions or in areas of higher consequence? | SCE does not differentiate ignition risks within its WRRM when determining mitigation options. Mitigation options are informed by an understanding of total risk by asset location. SCE assumes “inputs” to mean its inputs to its WRRM. SCE does not manually change the weighting of ignition sources based on certain conditions (e.g., climate conditions or in areas of higher consequence) as the model dictates the appropriate weighting of ignition sources. SCE differentiates between ignition risks by modeling each asset class separately. This results in a probability of failure for each piece of equipment in the field. This probability is “weighted,” or more accurately, calibrated, to the number of expected fires based on past fires attributed to the corresponding asset class. In this way, there is an expected frequency of fires at the specific asset level whose sum total of fires is aligned with historical fire counts attributed to that specific asset class. In other words, historical fire events are assigned to their causes, e.g., conductor, transformer, etc. The weighting that converts the probability of outage into frequency of ignition is based on these historical fire counts by classification. Mitigations are chosen by how effective they are at reducing the overall risk. SCE anticipates evolving its cross-mitigation optimization. Please see SCE’s 2021 WMP Update, Chapter 4, Section 4.3.10 for more details. | 2021-03-12 | 2021-03-17
CalAdvocates-SCE-2021WMP-13 | 001 | Using the table below, disaggregate the number of Level 1 findings in HFTD for detailed distribution inspections that were reported by SCE in Line 1.e of Table 1 of SCE’s non-spatial WMP data tables into each type of inspection that is included in line 1.e. | As noted in SCE’s response to CalAdvocates-SCE-2021WMP-09-008, the numbers in Table 1 contained errors. The below table contains the corrected numbers and the requested breakdown, based upon the data contained in SCE’s system of record. | 2021-03-15 | 2021-03-17
CalAdvocates-SCE-2021WMP-13 | 002 | Using the table below, disaggregate the number of Level 2 findings in HFTD for detailed distribution inspections that were reported by SCE in Line 1.h of Table 1 of SCE’s non-spatial WMP data tables into each type of inspection that is included in line 1.h. | As noted in SCE’s response to CalAdvocates-SCE-2021WMP-09-008, the numbers in Table 1 contained errors. The below table contains the corrected numbers and the requested breakdown, based upon the data contained in SCE’s system of record. | 2021-03-15 | 2021-03-17
MGRA-SCE-007 | 001 | On p. 47 of its WMP, SCE states that: “To account for a wide range of historical climate scenarios, SCE uses 41 weather scenarios across a 20-year historical climatology in its WRRM consequence model. By using a wide range of models, SCE can determine the relative risk of wildfire consequence for each location under the maximum likely weather conditions, based on a historic climatology for any given location.” Are the same “maximum likely weather conditions” used for modeling fire spread identical to those that are used by the Probability of Ignition (POI) model? In other words, are the same weather condition assumptions used to feed both POI and consequence models? |  | 2021-03-16 | 2021-03-19
MGRA-SCE-007 | 002 | On p. 47 of its WMP, SCE states that: “To account for a wide range of historical climate scenarios, SCE uses 41 weather scenarios across a 20-year historical climatology in its WRRM consequence model. By using a wide range of models, SCE can determine the relative risk of wildfire consequence for each location under the maximum likely weather conditions, based on a historic climatology for any given location.” Are the ignition probability and consequence probability treated as completely independent distributions? Aside from location, are there any input parameters common between the two calculations (such as weather)? |  | 2021-03-16 | 2021-03-19
MGRA-SCE-007 | 003 | In its comments on the 2020 WMPs, MGRA noted that there were significant differences between the 99th percentile results from PG&E and SCE meteorology models in areas where model predictions overlapped. Did SCE consult with PG&E on weather model differences in 2020 and if so what was their conclusion regarding differences between their models, particularly with regard to 99th percentile wind discrepancies? |  | 2021-03-16 | 2021-03-19
MGRA-SCE-007 | 004 | Please provide a table of all Utility Maturity Survey responses that have changed since 2020, how they have changed, and a description of why. |  | 2021-03-16 | 2021-03-18
TURN-SCE-008 | 001 a. | In SCE Response to TURN-DR-003-01 SCE provided pole inventory by class size using standard pole size classification. In its GRC workpapers (WPSCE04V05APt01, p. 259 of the workpapers), SCE calculates a unit cost for covered conductor by using 605 poles disaggregated into five “load cases.” The study header states “HFRA Pole Sample Mixed Large Small Study – Extract.” a. Please explain the meaning of the “pole sample mixed large small” header in the workpaper? At a minimum, please include in the explanation: i. Which pole size classes were included in the sample? ii. Please provide the approximate percentage of each pole class in the sample, using the standard pole size classification provided in TURN-03 Question 1 in Excel. iii. Please explain how the sample compares to SCE’s pole sizes in HFRA, as provided in the previous DR. | SCE objects on the grounds that this question seeks information which is outside the scope of this proceeding. Notwithstanding this objection, SCE responds as follows: 1a - The term “pole sample mixed large small” in the header of the workpaper refers to wires in the study, and refers to the fact the study had a mix of small and large wire. 1ai – The sample included the following classes: 5, 4, 3, 2, 1, H1, H2, H3, H5, H6 and EH10. 1aii – The below table contains the count and percentage of the poles contained in the sample: Tables 1aiii – The study is directionally correct with the pole break down by Class on SCE system in 2018, when the study was performed. Certain pole classes have a higher representation (such as Classes 4 and 5) and other pole classes have a lower representation (such as Classes 1 and 2) in the sample compared to the population per SCE’s system of record. | 2021-03-16 | 2021-03-19
TURN-SCE-008 | 001 b. | In SCE Response to TURN-DR-003-01 SCE provided pole inventory by class size using standard pole size classification. In its GRC workpapers (WPSCE04V05APt01, p. 259 of the workpapers), SCE calculates a unit cost for covered conductor by using 605 poles disaggregated into five “load cases.” The study header states “HFRA Pole Sample Mixed Large Small Study – Extract.” b. Please explain the meaning of each of the five “load cases” in the GRC workpaper. At a minimum: i. Please explain what the weights refer to, including but not limited to whether and how exactly they relate to pole size. ii. If the weights do not relate to pole size, please explain why SCE does not believe pole size is a relevant factor to estimate the additional number of pole replacements needed to install covered conductor. iii. If the weights do not relate to pole size, please explain if and how the load cases reflect the presence of any particular type of conductor and/or other assets on the pole. iv. Please explain and illustrate how existing HFRA pole size was incorporated into the SCE GRC workpaper to estimate additional pole replacements. v. Please explain if and how the “load case” numbers correspond at all to pole size classification. This may also support SCE’s response to question 1(ii) above. | SCE objects to this question on the grounds that it seeks information outside the scope of this proceeding. Notwithstanding this objection, SCE responds as follows. b. The five load cases in the GRC workpaper refer to the five types of wind loading across SCE’s territory, which are: Light 8lb and Heavy 6lb, 12lb, 18lb, and 24lb. i. The weights refer to the increase weights of covered conductor over bare conductor in pounds per linear foot. This weight is not related to pole size. ii. SCE does believe that pole size is relevant to estimate the additional number of pole replacements needed to install covered conductor. The study took a random sample of poles across various heights and classes to determine if the increased weight and cross-sectional area of covered conductor would make a pole fail pole loading with covered conductor installed. iii. The load cases represent wind loading in various areas across SCE’s territory. Due to the increased weight and cross-sectional area of covered conductor, these wind loading cases have varying effects on pole loading. iv. In the workpaper, SCE used a random sampling of existing pole configurations with the change from bare conductor to covered conductor to determine the impact on pole loading when covered conductor is installed. v. The load case does not correspond to pole size but rather to wind loading. In areas with high wind loading, larger class poles may need to be installed to support the additional forces imparted by higher wind loads. | 2021-03-16 | 2021-03-19
WSD-SCE-005 | 001 | How is the RSE value for covered conductor installation calculated? Provide a breakdown on how the reduction in risk for system hardening is determined, and how the RSE value is determined based on that risk reduction value. Include all associated work papers and inputs into the final value. | The RSE value for covered conductor is calculated in the same manner as the RSE calculations for all other mitigations. As stated in WMP pages 63-64 the RSE is calculated as follows: 1. Use historical counts to forecast baseline (in the absence of mitigations) wire-down, outage, and CPUC ignition levels. 2. For each program, obtain a. cost forecast, b. mitigation effectiveness – a percentage between 0 and 100% denoting the effectiveness of reducing risk driver frequency or consequences of events, c. prospective units to be installed/performed, and d. years of useful life (mean time to failure) 3. For each year, calibrate the WRRM to the forecast baseline wire-down, outage, and CPUC ignition levels to convert probabilities to frequencies. 4. Where available, use location data, mitigation effectiveness, and the WRRM to estimate risk buydown associated with the program. a. If location data are not available, or if the scope is not determined yet, use the risk buydown curve from the Wildfire Risk Reduction Model. Use the units to be installed/performed in that year to determine how far down the risk buydown curve the program may mitigate risk. b. Apply the mitigation effectiveness to the particular asset’s risk drivers or consequences and compare the resulting risk with the baseline risk. The difference is the risk reduction. 5. Calculate the net present value (NPV) of the risk reduction applying the years of useful life as the time horizon. 6. Calculate the RSE by dividing the NPV of risk by the cost forecast. In particular, for covered conductor, the risk reduction is determined by calculating the risk without the covered conductor at the circuit segment minus the risk with the covered conductor as part of the calculation of the NPV. Attached you will find code that calculates the RSE values (WSD_SCE_005_Q1_cc_rse.R) as well as inputs necessary for the calculation: The filename is CONFIDENTIAL_WSD_SCE_005_Q1_work_inputs_and_output.xlsx. • Excel sheet cc_mitigation_effectiveness has consequence and Subdriver mitigation effectiveness. The risk reduction calculation incorporates the mitigation effectiveness subdrivers that are captured by our risk model inventory. • Excel sheet cc_units_spend contains nits deployed and cost forecast for 2021-2022, as well as useful life. • Excel sheet seg_consequences has fire and psps consequence scores for each segment. • Excel sheet segment_foi_by_subdriver contains Expected ignition counts by subdriver for each segment, already converted from WRRM probabilities to frequencies and calibrated to historical ignition baseline. • Excel sheet cc_compl_segs_20210112 gives a List of locations where CC has been installed. CONFIDENTIAL | 2021-03-16 | 2021-03-19
WSD-SCE-005 | 002 | How did SCE calculate the risk reduction value for covered conductor installation, in terms of the percent effectiveness? Include all associated work papers and inputs into the final value. | Please refer to SCE’s response to Question 1 for details on the methodology for calculating the overall risk reduction value. Please note that the risk reduction value for covered conductor in the 2021 WMP Update combined the mitigation effectiveness of covered conductor and Fire Resistant (FR) poles. To determine the percent effectiveness of covered conductor, SCE evaluated the ability for covered conductor to address each risk driver. Subject Matter Expert (SME) judgment was used to determine the mitigation effectiveness of covered conductor; this judgement was informed by benchmarking, analysis, and testing. This is expounded upon in detail in the attached deck entitled “Covered Conductor Compendium.” Table 1 and Table 2, below, explain the reasoning behind the effectiveness values established for each driver. Table 1 includes only the covered conductor values and not the combined covered conductor and FR pole values used in the risk reduction calculation. Table 2 includes only the FR pole mitigation effectiveness values. Additionally, mitigation effectiveness values at 0% or that were not applicable were omitted from both tables. The attached Excel file entitled “CC and FR Pole ME” details the combined mitigation effectiveness data. | 2021-03-16 | 2021-03-19
MGRA-SCE-008 | 001 | Regarding the use of the Technosylva fire spread model and its use to calculate wildfire consequences: How is the duration of the simulation determined for risk calculations used to prioritize circuit risks for mitigation? Is there a maximum / default duration of simulation for this purpose and if so what is it? | For wildfire mitigation planning, SCE uses the maximum modeled consequences across 41 weather scenarios for ignition simulations with an eight (8) hour propagation period. A standard eight (8) hour duration was chosen to allow for comparison of relative consequences across all assets. These consequence scores are, in turn, used to prioritize the deployment of mitigations. | 2021-03-17 | 2021-03-22
MGRA-SCE-008 | 002 | Regarding the use of the Technosylva fire spread model and its use to calculate wildfire consequences: Is there a maximum wildfire size used for simulation determined for risk calculations used to prioritize circuit risks for mitigation and if so what is it? | No, there is no maximum fire size used for simulations that determine risk calculations. | 2021-03-17 | 2021-03-22
MGRA-SCE-008 | 003 | Regarding the use of the Technosylva fire spread model and its use to calculate wildfire consequences: How are weather and fuel inputs determined for risk calculations used to prioritize circuit risks for mitigation? | SCE has chosen 41 historical weather events to represent fire consequence across the SCE service area. These scenarios are used to inform the prioritization of wildfire mitigation efforts for circuits. These weather events were chosen based on the magnitude and duration of each weather event over the past 20 years. Technosylva uses the following weather and fuels inputs for fire spread modeling: Wind speed Relative humidity Temperature Dead fuel moisture Live fuel moisture The above weather and fuel variables were used to calculate fire spread and consequence for each of the weather events which were then aggregated to provide a risk single score along each circuit. | 2021-03-17 | 2021-03-22
MGRA-SCE-008 | 004 | Regarding the use of the Technosylva fire spread model and its use to calculate wildfire consequences: How is the duration of the simulation determined for risk calculations used to identify circuits for PSPS? Is there a maximum / default duration of simulation for this purpose and if so what is it? Or does the duration of the simulation extend to the projected length of the weather event? | SCE does not use Technosylva to identify circuits for PSPS. | 2021-03-17 | 2021-03-22
MGRA-SCE-008 | 005 | Regarding the use of the Technosylva fire spread model and its use to calculate wildfire consequences: Is there a maximum wildfire size used in simulations to identify circuits for PSPS and if so what is it? | SCE does not use Technosylva to identify circuits for PSPS. | 2021-03-17 | 2021-03-22
TURN-SCE-009 | 001 | In SCE Response to TURN-SCE-006, Question 006, SCE stated “the covered conductor program unit costs in the 2021 WMP included Fire Resistant Poles, whereas those costs were accounted for separately in SCE’s 2021 GRC unit costs.” a. Please disaggregate the 2021 WMP unit cost per circuit mile to isolate the Fire Resistant Pole incremental cost over wood poles used in the 2021 WMP unit cost per circuit mile. In other words, what is the recorded cost of covered conductor ($/circuit mile) if SCE had installed wooden poles instead of “fire resistant” poles. Please provide all workpapers and assumptions. b. Is the Fire Resistant Pole cost identified in subpart (a) above the same as the cost for Fire Resistant Poles relied on when developing the 2021 GRC? c. If the answer to subpart (b) is no, please identify the Fire Resistant Pole cost relied on in the 2021 GRC request? d. If the answer to subpart (b) is no, please explain the reason for difference between the two forecasts. | SCE objects to this question on the following grounds: (1) the question seeks general rate case/cost recovery information that is outside the scope of this proceeding under Public Utilities Code Sections 8386 & 8386.4(b)(1); (2) the question seeks information not relevant to evaluation of SCE’s Wildfire Mitigation Plan; (3) the question seeks information not reasonably likely to lead to WMP comments that would be appropriate under Public Utilities Code Section 8386(d); (4) the question seeks information that is not readily available and would be unduly burdensome for SCE to assemble and provide; and (5) there is no support for this question under Resolution WSD-001 or the “Wildfire Safety Division Guidance on Resolution WSD-001 and Data Request Best Practices” (January 29, 2021). Based on the foregoing, SCE does not intend to provide a substantive response to this question. | 2021-03-18 | 2021-03-23
TURN-SCE-009 | 002 | In the response to TURN-SCE-006, Q4, SCE indicates that covered conductor will reduce approximately 64% of HFRA wildfire risk. The risk curve provided in response to TURN-SCE-007, Q1 appears to show a risk reduction to approximately less than 20% (.2) at the 4,000 mile mark of HFRA Circuit Mileage. a. Please explain this apparent contradiction. Provide all relevant workpapers and calculations b. Does SCE contend that mitigation effectiveness for their proposed mitigations can eliminate wildfire risk? If not, why does the curve show a reduction of risk to zero? c. Please provide the workpapers that shows the “risk bought down” for each circuit mile in the curve provided in response to TURN-SCE-007, Q1. d. If SCE does not expect 100% mitigation effectiveness from its mitigation measures, please provide the expected amount of risk (in percentage terms) that will remain in SCE’s HFRA after covered conductor is deployed. Please explain how this was calculated and provide all workpapers in Excel. | a) The curve in SCE’s response to TURN-SCE-007, Q1 reflects the wildfire risk for each circuit segment in HFRA associated with conductor without any mitigations applied. SCE’s response to TURN-SCE-006, Q4 reflects the deployment of covered conductor in consideration of its mitigation effectiveness and any constructability/feasibility issues associated with the scope. Please note that some of this deployment scope was based on prior risk models. For workpapers and calculations related to covered conductor mitigation effectiveness, please refer to SCE’s response to TURN-SCE-006, Q4 submitted on March 17, 2021. The requested workpapers may be found in the attachments to SCE’s response, which is the Excel spreadsheet entitled “004_CONFIDENTIAL_TURN-SCE-006_Q3_Q4_workpaper_20210317.xlsx,” and the R programming script entitled “004_01_turn_sce_006_q3_q4_workpaper_script_20210317.R.” For the workpapers on the risk curve, please see SCE’s response to part c) of this Question in this response. b) No. As discussed in part a), SCE clarifies that the curve in SCE’s response TURN-SCE-007, Q1 reflects the wildfire risk for each circuit segment in HFRA associated with conductor without any mitigations applied. c) For the risk curve workpapers, please see the Excel spreadsheet entitled “004_CONFIDENTIAL_TURN-SCE-006_Q3_Q4_workpaper_20210317.xlsx” that was attached to SCE’s response to TURN-SCE-006, Q4 submitted on March 17, 2021. d) SCE estimates the remaining risk to be approximately 36% based on evaluation of the scope of work identified in the 2020-2022 WMP (4,000 miles). This estimate is based on the analysis used to respond to TURN-SCE-006, Q4 and uses the same response’s workpapers. | 2021-03-18 | 2021-03-23
TURN-SCE-009 | 003 | Is the only difference between the risk curves relied on in SCE’s 2021 GRC Filing and the 2021 WMP reliance on the updated methodology at the circuit segment level? a. Table 4-4 of SCE’s Wildfire Mitigation Plan identifies that the WF consequence Component was based on the Reax Consequence in 2019 and the Technosylva Consequence in 2020 is this the updated methodology at the circuit segment level referenced in TURN-SCE-007, Q 1 (c)? b. If the answer to subpart (a) is no, please provide a citation to the discussion of this updated methodology in SCE’s 2021 WMP. c. To the extent SCE’s risk analysis has significantly changed the prioritization of circuits in its HFRA compared to the GRC analysis, please explain and quantify by how much. Please include in the explanation why the Reax and Technosylva results differed dramatically in some instances. Please provide all workpapers and calculations. d. Please explain whether SCE will from this point forward use the WMP risk analysis to prioritize circuits for covered conductor deployment or whether it will still use the GRC analysis. Please provide the date at which SCE finished this analysis, and whether this immediately informed SCE’s prioritization of covered conductor deployment, | SCE objects to this question on the following grounds: (1) the question seeks general rate case information that is outside the scope of this proceeding under Public Utilities Code Sections 8386 & 8386.4(b)(1); (2) the question seeks information not relevant to evaluation of SCE’s Wildfire Mitigation Plan; (3) the question seeks information not reasonably likely to lead to WMP comments that would be appropriate under Public Utilities Code Section 8386(d); and (4) there is no support for this question under Resolution WSD-001 or the “Wildfire Safety Division Guidance on Resolution WSD-001 and Data Request Best Practices” (January 29, 2021). Notwithstanding these objections, SCE responds as follows: No, there are several differences between the risk curves relied on in SCE’s 2021 GRC Filing and the 2021 WMP beyond the updated methodology. a) No, the response to TURN-SCE-007, Q1(c) does not employ the same methodology as described in Table 4-4 of SCE’s 2021 WMP Update. The risk curve in TURN-SCE-007, Q1(c) was developed using Technosylva consequence and the contact-with-foreign object model and the equipment facility failure model were calibrated using forecasts of ignitions. Conversely, Table 4-4 describes a model that includes PSPS probability and consequence components, which were not included in the risk curve calculation used in TURN-SCE-007, Q1(c). b) For the methodology used to provide a response to TURN-SCE-007, Q1(c), please see the Ignition Consequence Models discussed in Section 4.3.6 on page 57 and the Probability of Ignition Models discussed in Section 4.3.5 on page 56 of SCE’s 2021 WMP Update. Calibration of the WRRM to the forecasted baseline for wire-down, outage, and CPUC ignition levels is briefly mentioned in part 3 of the RSE Calculation Method discussed in Section 4.3.8 on page 63. c) SCE disagrees with the characterization of the terms “significantly changed” and “dramatically.” For a quantification of the changes, see the Sankey chart in SCE’s response to SCE-5 Action Statement1 which quantifies the extent to which prioritization changes due to the shift from Reax to Technosylva. As stated in SCE’s 2021 WMP Update, In 2020, SCE transitioned to a Technosylva-based consequence model, which included improvement over the Reax-based consequence model. Key improvements include updated and more granular model inputs (e.g., buildings, assets, fuels, population), more advanced fire propagation techniques (e.g., urban encroachment), and direct mapping of consequence scores to individual assets. Technosylva fire spread model uses individual building footprints, population count, SCE asset data, and a 20-year climatology and surface fuel data specifically calibrated to SCE’s service area. This will enable SCE to re-run this simulation on an annual, or semi-annual, basis based on updated and calibrated information from previous fire weather seasons which is a significant improvement from the Reax models in targeting mitigations to HFRAs. Please see Table SCE 4-5 for a list of model inputs, outputs, and algorithms.2 For information on the differences in risk prioritization from Technosylva and the prior model, please refer to SCE’s response to the WSD’s data request WSD-SCE-004 Q9, submitted on March 17, 2021. d) SCE is now using the WMP risk analysis to help prioritize future deployment of covered conductor that will likely be deployed in 2022 or beyond. Because scoping, designing, permitting, constructing, etc. covered conductor can take substantial time – often greater than 12 months – current covered conductor scope in 2021 is based on prior risk analysis methods. This allows for meaningful and substantial risk reduction to occur while new scope is positioned for future deployment based on the latest risk modeling capabilities. All versions of the risk modeling are focused on HFRA, which the Commission deems to be inherently risky. | 2021-03-18 | 2021-03-23
TURN-SCE-009 | 004 | Regarding the risk curve relied on in SCE’s 2021 GRC: a. Does it “show that risk is not uniform and some segments exhibit significantly more wildfire risk than others”? b. Does it show “the risk associated with each circuit may not be uniform along its length”? | SCE objects to this question on the following grounds: (1) the question seeks general rate case information that is outside the scope of this proceeding under Public Utilities Code Sections 8386 & 8386.4(b)(1); (2) the question seeks information not relevant to evaluation of SCE’s Wildfire Mitigation Plan; (3) the question seeks information not reasonably likely to lead to WMP comments that would be appropriate under Public Utilities Code Section 8386(d); and (4) there is no support for this question under Resolution WSD-001 or the “Wildfire Safety Division Guidance on Resolution WSD-001 and Data Request Best Practices” (January 29, 2021). Based on the foregoing, SCE does not intend to provide a substantive response to this question. | 2021-03-18 | 2021-03-23
TURN-SCE-009 | 004 Supplemental | Regarding the risk curve relied on in SCE’s 2021 GRC: a. Does it “show that risk is not uniform and some segments exhibit significantly more wildfire risk than others”? b. Does it show “the risk associated with each circuit may not be uniform along its length”? | SCE objects to this question on the following grounds: (1) the question seeks general rate case information that is outside the scope of this proceeding under Public Utilities Code Sections 8386 & 8386.4(b)(1); (2) the question seeks information not relevant to evaluation of SCE’s Wildfire Mitigation Plan; (3) the question seeks information not reasonably likely to lead to WMP comments that would be appropriate under Public Utilities Code Section 8386(d); and (4) there is no support for this question under Resolution WSD-001 or the “Wildfire Safety Division Guidance on Resolution WSD-001 and Data Request Best Practices” (January 29, 2021). Notwithstanding this objection, SCE responds as follows: a) By “uniform,” SCE interprets that as “uniformly distributed,” which means risk=c where c is a constant value. Yes, risk is not uniform and some segments exhibit higher wildfire risk than others. Because the risk can vary among different segments across different circuits, especially if circuits traverse HFTD tiers and the circuit segments are exposed to different probabilities of ignition by contact from objects, or varying topography and vegetation that can influence fire propagation and consequence. If the risk is uniform among all segments on all circuits, then the risk curve would be closer to a straight line. b) By “uniform,” SCE interprets that as “uniformly distributed,” which means risk=c where c is a constant value. Yes, the risk associated with each circuit may not be uniform along its length. A typical circuit has many connected segments and risk can vary among them, especially if that circuit traverses HFTD tiers and is exposed to different probabilities of ignition by contact from objects, or varying topography and vegetation that can influence fire propagation and consequence. If the risk is uniform among all segments on all circuits, then the risk curve would be closer to a straight line. | 2021-03-18 | 2021-03-26
CalAdvocates-SCE-2021WMP-14 | 001 | For each Risk Spend Efficiency (RSE) in the “New/Revised RSE (Tier 3)” column in Table SCE 9.8-3, provide the mitigation effectiveness associated with that mitigation. | All mitigations calculated for the Revision Notice in Table SCE 9.8-3 can be categorized into three general groupings: Distribution fire risk sub-driver mitigations, Transmission fire risk sub-driver mitigations, and mitigations that mitigate the consequences related to PSPS risk. The mitigation effectiveness percentages for Distribution fire risk sub-driver mitigations are listed in Table 1 and include the following mitigations: • Ground Inspections/Remediations - Distribution • Aerial Inspections/Remediations - Distribution • Fire Resistant Poles • Covered Conductor The mitigation effectiveness percentages for Transmission fire risk sub-driver mitigations are listed in Table 2 and include the following mitigations: • Ground Inspections/Remediations - Transmission • Aerial Inspections/Remediations - Transmission • C-Hooks Weather Stations and Sectionalizing Devices mitigate consequences related to PSPS risk. Both programs have a 44.65% mitigation effectiveness on safety, reliability, and financial components of PSPS MARS consequence. Table | 2021-06-07 | 2021-06-10
CalAdvocates-SCE-2021WMP-14 | 002 | For each RSE mitigation effectiveness provided in response to Question 1, explain the factors that SCE used to determine the mitigation effectiveness. | For the Distribution and Transmission ground and aerial inspection/remediation programs, all of the mitigation effectiveness percentages that are listed in Response 001 consider the number of notifications remediated and outage events observed per sub-driver. The mitigation effectiveness for each sub-driver was calculated using the following formula: Mitigation Effectiveness = (P1 Notifications Remediated + P2 Notifications Remediated) / (P1 Notifications Remediated + P2 Notifications Remediated + Faults) Regarding the explanation of mitigation effectiveness for Covered Conductor and Fire Resistant Poles, please see Attachment 1. For C-Hooks, engineering expertise was used to determine mitigation effectiveness. Table 1, below, explains the reasoning for each sub-driver that was both applicable and non-zero. Table For sectionalizing devices and weather stations, the following logic was applied. In 2020, SCE’s sectionalizing efforts helped avoid over 203,409 customer outages, which represents an estimated 47% decrease from the number of outages the impacted circuits would have otherwise experienced. This was calculated by comparing the total customer count of circuits de-energized with the actual count of customers de-energized, yielding the customers that remained energized through sectionalization during a de-energization activities. SCE uses live weather station data in an overwhelming majority of its PSPS de-energization decisions. The situational awareness of conditions across a particular circuit, which these weather stations provide, is a crucial enabler in allowing SCE to utilize sectionalizing devices and keep portions of a circuit energized, when appropriate. SCE ascribed a 95% mitigation effectiveness value to our network of weather stations. SCE may utilize live field observations (LFO) to gather information about circuit conditions in rare cases where weather stations are not the primary decision drivers in a de-energization decision. For mitigations where LFO instead of weather station data are used, SCE assigned a mitigation effectiveness of 5%. The sectionalizing devices in conjunction with the weather stations will allow SCE to perform PSPS in between sectionalizing devices to reduce PSPS impacts, therefore the combined mitigation effectiveness for the two is 47%*95%=44.65%. | 2021-06-07 | 2021-06-10
CalAdvocates-SCE-2021WMP-14 | 003 | On pages 618 and 619 of the revised 2021 WMP Update (redlined), SCE states that the aggregated RSE for Community Resource Centers (CRC) and Community Crew Vehicles (CCV) is 188. Similarly, SCE states that Critical Care Battery Backup (CCBB) has an RSE of 22. SCE also mentions that CCBB does not reduce wildfire risk or consequence but does reduce the consequence of PSPS. a) When calculating the RSE for Customer Care programs, what historical counts are used as a forecast baseline per the process SCE describes on page 66 of its revised 2021 WMP Update (redlined)? b) What is the mitigation effectiveness of the CRC, CCV, and CCBB programs? c) Describe how the mitigation effectiveness of the CRC, CCV, and CCBB programs is determined. d) Describe all other factors or metrics used in the calculation of RSE for CRC, CCV, and CCBB programs. | a) The Customer Care programs reduce PSPS risk through consequence mitigation, as the provided resources alleviate the impact of de-energizations on customers. As such, the RSE is quantified in part by calculating PSPS risk reduction on all HFRA PSPS circuits. To calculate the baseline PSPS risk, SCE uses the risk bowtie framework to calculate the relative risk of PSPS impacts. On the left hand of the bow tie is the probability of de-energization which is based on a 10-year back casting of historical wind and weather conditions to estimate the annual frequency and duration of de-energization events, using the current PSPS de-energization protocols. On the right side of the bowtie, SCE estimates the safety, reliability, and financial consequences to the customers due to a PSPS de-energization. The PSPS risk calculated by the risk bowtie approach serves as the basis for risk reductions and is therefore used in RSE calculations. b) CRCs/CCVs are estimated to have a 1% mitigation effectiveness on all safety, reliability, and financial components of PSPS MARS consequence. CCBB has mitigation effectiveness percentages which vary depending on the circuit under consideration. For all components (financial, reliability, safety) of PSPS consequence, there is a 33% mitigation effectiveness which is further multiplied by 25% (the estimated enrollment rate) and the proportion of medical baseline customers of all customers on the circuit. The safety component is further multiplied by the circuit’s access and functional needs (AFN) multiplier since that considers the target population of the program. c) For CRC/CCV, Subject Matter Expert (SME) judgment was used to determine the mitigation effectiveness. Based on the intent to cover all of HFRA, a broad geographic area, it was reasonable to conclude that these resources will have a net positive benefit when deployed during a PSPS event and will mitigate the consequence of PSPS events on the community, but difficult to precisely quantify given the limited data available. The mitigation effectiveness of CCBB is driven by two main factors, the number of batteries supplied and the duration benefit of each battery. For purposes of calculating the RSE as part of its 2021 WMP Update, SCE assumed that approximately 25% of total eligible customers would choose to enroll in the program. The batteries on average have an 8-hour battery life, based on an analysis of total usage hours in over 300 customer assessments, 1 which estimates coverage of about 33% over the normal duration of a PSPS event (a PSPS event is assumed to last 24 hours on average). d) In addition to utilizing the baseline PSPS risks and applying the mitigation effectiveness percentages to the entire HFRA for CRC/CCV and to all circuits with medical baseline customers who live in HFRA for CCBB, the useful life of each mitigation is also considered to calculate the net present value (NPV) of the risk reduction. The NPV of risk reduction is divided by the cost forecast to arrive at the RSE for each mitigation. The useful life of CRC/CCV is 1 year since these resources are only available to customers around/during the time of the de-energization. The useful life of CCBB is 3 years because the program provides a 3-year warranty for the battery and solar panel kit. | 2021-06-07 | 2021-06-10
CalAdvocates-SCE-2021WMP-14 | 004 | On page 577 of the Revised 2021 WMP Update (redlined), SCE states that weather stations combined with sectionalizing devices have an RSE of 598. a) When calculating the RSE for the above mitigations, what historical counts are used as a forecast baseline per the process SCE describes on page 66 of its revised 2021 WMP Update (redlined)? b) What is the mitigation effectiveness of the weather station and sectionalizing devices mitigation activities? c) Describe how the mitigation effectiveness of weather station and sectionalizing devices is determined. d) Describe all other factors or metrics used in the calculation of RSE for weather station and sectionalizing devices mitigation activities. | Weather Stations and Sectionalizing Devices can mitigate PSPS risk. To calculate the baseline PSPS risk, SCE uses the risk bowtie framework to calculate the relative risk of PSPS impacts. On the left hand of the bow tie is the probability of de-energization which is based on a 10-year back casting of historical wind and weather conditions to estimate the annual frequency and duration of de-energization events using the current PSPS de-energization protocols. On the right side of the bowtie, SCE estimates the safety, reliability, and financial consequences to customers due to a PSPS de-energization. The PSPS risk calculated by the risk bowtie approach serves as the basis for risk reductions and is therefore used in RSE calculations. b) Both programs have a 44.65% mitigation effectiveness on all components (safety, reliability, and financial) of PSPS MARS consequence. c) In 2020, SCE’s sectionalizing efforts helped avoid over 203,409 customer outages, which represents an estimated 47% decrease from the number of outages the impacted circuits would have otherwise experienced. This was calculated by comparing the total customer count of circuits de-energized with the actual count of customers de-energized, yielding the customers that remained energized through sectionalization during a de-energization activities. SCE uses live weather station data in an overwhelming majority of its PSPS de-energization decisions. The situational awareness of conditions across a particular circuit, which these weather stations provide, is a crucial enabler in allowing SCE to utilize sectionalizing devices and keep portions of a circuit energized, when appropriate. SCE ascribed a 95% mitigation effectiveness value to our network of weather stations. SCE may utilize live field observations (LFO) to gather information about circuit conditions in rare cases where weather stations are not the primary decision drivers in a de-energization decision. For mitigations where LFO instead of weather station data are used, SCE assigned a mitigation effectiveness of 5%. The sectionalizing devices in conjunction with the weather stations will allow SCE to perform PSPS in between sectionalizing devices to reduce PSPS impacts, therefore the combined mitigation effectiveness for the two is 47%*95%=44.65%. d) In addition to utilizing the baseline PSPS risks and applying the mitigation effectiveness percentages, the useful life of each mitigation is also considered to calculate the net present value (NPV) of the risk reduction. The NPV of risk reduction is divided by the cost forecast to arrive at the RSE for each mitigation. The useful lives for weather stations and sectionalizing devices are 20 years, based on an estimate from SMEs, taking into account operational considerations, vendor input, and authorized service lives. | 2021-06-07 | 2021-06-10
WSD-SCE-006 | 001 | Regarding Cal Advocate’s 71 “riskiest circuits” within SCE’s Redlined 2021 WMP Update, on p. 629, SCE states that “SCE’s current 2021 plan for those circuits is 694 miles”. a. Why did SCE’s plan change from 581 miles to 694 miles? b. Is the change in mileage from 581 to 694 due only to the addition of more high risk circuits, or were any originally scoped high risk circuits removed? If some were removed, provide the mileage and associated circuits. c. Is 1,883 still the total for planned mileage? If not, provide the updated total. | a. Subsequent to the time that SCE responded to Cal Advocates’ data request that informed its Cal Advocates’ Comments and WSD’s Revision Notice on this subject, SCE increased the circuit-segment mileage planned to be “completed” in 2021 associated with the Cal Advocates-identified 71 “riskiest circuits” from 581 to 694 to ensure coverage of complete segments on those circuits to reduce and/or mitigate PSPS events. In doing so, SCE is simultaneously reducing overall wildfire ignition risk and reducing and/or mitigating PSPS events on those circuits. It is important to note that, in this context, “complete” means mileage scoped for executable planned work, not necessarily the amount of covered conductor that SCE will actually install, as the latter will almost certainly be a lower number due to permitting constraints, environmental restrictions, and other operational realities. b. The change in mileage did not include or remove any circuits from the Cal Advocates-identified 71 “riskiest circuits” list. The increase in mileage reflects an increase in circuit-segment miles that are planned to be completed on those same 71 circuits and, further, is completely unrelated to the addition of any other high-risk circuits. c. The 1,883 circuit miles was the total available and executable planned mileage for 2021 at the time of the original data request on March 16, 2021. Due to myriad factors—including but not limited to operational constraints, permit availability, and environmental challenges--SCE’s total available and executable planned mileage varies month to month. SCE plans to fully complete (i.e., install) between 1,000 and 1,400 circuit miles in 2021 as detailed in our 2021 WMP filing. Any miles that are part of the 1,883 initial available and executable planned scope that are not completed in 2021 will likely be completed in 2022, barring any external challenges that SCE is unable to mitigate. As discussed in more detail in response to WSD-SCE-006 Question 2, SCE’s current completed and estimated available and executable planned mileage for 2021 (i.e., completed and “scoped”, respectively) is approximately 2,200 circuit segment miles. | 2021-06-21 | 2021-06-24
WSD-SCE-006 | 002 | Relating to Figure SCE 9.10-4 of SCE’s Redlined 2021 WMP Update: a. What circuit mileage and percentage of the 1,883 miles of planned covered conductor projects are within SCE’s first 1,250 mile risk tranche? b. What circuit mileage and percentage of the 1,883 miles of planned covered conductor projects are within SCE’s second 2,500 mile risk tranche? c. Provide the same graph broken down by planned date of installment (i.e. when SCE intends to install the scoped CC indicated within the graph, broken down by year of installation). Include the associated circuit mileage numbers. d. Provide the number of circuit segments that fall under each of the circuit mile tranches. | a. As explained in WSD-SCE-006 Q1c, SCE’s planned mileage could change due to the various factors mentioned, and this varies from month to month. Currently, the available miles scoped for 2021 is approximately 2,200 miles. Of those, approximately 550 circuit miles is in the first 1,250 mile risk tranche (25% of the approximately 2,200 circuit miles). It should be noted that prior to 2021, SCE has already completed installation of approximately 240 circuit miles in the first risk tranche. b. Similarly, approximately 450 circuit miles is in the second 1,250 risk tranche (~20% of the approximately 2,200 circuit miles). It should be noted that prior to 2021 SCE has already completed installation of installation of approximately 210 circuit miles in the second risk tranche. c. As of June 23, 2021 the covered conductor installation and scope1 is shown in the graph below. The graph is broken out as requested by scope year. Changes made to this graph, aside from the requested visual representation, reflect the increased amounts of installed covered conductor circuit miles since SCE’s Revised 2021 WMP was submitted. As shown in the graph, the majority of the highest wildfire risk circuit segment miles have been prioritized for installation first. Nonetheless, 1 By “scoped” SCE means circuit mile segments that are available and executable for installation. For example, “Scoped for 2021” means circuit mile segments available for construction in 2021. this plan data represents a point in time, 2 and the plan is regularly reevaluated based on risk model updates and conditions in the field. SCE expects to complete a refreshed analysis within the next month to assess how much of the currently modeled highest wildfire risk circuit segment miles currently shown to scoped for later than 2022 can potentially be accelerated for covered conductor installation in 2022. If those efforts prove viable, SCE will evaluate postponing the installation of relatively lower risk circuit segment miles currently scoped for 2022 until later years. Graph and Table | 2021-06-21 | 2021-06-24

## WMP Supporting Documents
DOCUMENT TITLE | DATE | TYPE
SCE's Wildfire Mitigation Plan.pdf | 2021-02-05 | Wildfire Mitigation Plan
Southern California Edison’s 2021 Wildfire Mitigation Plan Update Supplemental Filing | 2021-02-26 | Wildfire Mitigation Plan
Southern California Edison Q4 2020 Quarterly Data Report | 2021-02-05 | Wildfire Mitigation Plan
Southern California Edison Company’s Comments on Wildfire Safety Division’s Draft Compliance Operational Protocols | 2021-01-22 | Wildfire Mitigation Plan
SCE's Comments on Draft 2021 Guidance on Engagement of Independent Evaluators | 2021-03-24 | Wildfire Mitigation Plan