## Sheet1
CalAdvocates-SCE-2022WMP-02
Associated Circuit Name | Defect Type | Description of Defect | WMP Initiative Associated with Defect | Date Defect Was Identified | Date Defect Was or Will Be Corrected | Priority Level of Corresponding Corrective Tag2 | Location of Defect (Latitude/Longitude)
Horntoad | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | The pole is surrounded by vegetation. There are vines growing on Guywire above insulator, which is a defect. | WMP5-Vegetation Management and Inspections | 2021-01-14 | 2021-02-08 | P2 | 34.1389186, -118.6202717
Porcelain | 319.1 Data provided by utility does not reflect conditions in the field. | The severity of the defect of inconsistent information between tracking spreadsheet and field observation (Defect Code: 319.1) is Minor. | WMP3-Grid Design and System Hardening | 2021-02-09 | 2021-02-24 | N/A | 33.8042043, -117.5153544
Cachuma | 423.1 Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Loose down guy. The severity of this defect is Minor. | WMP4-Asset Management and Inspections | 2021-02-09 | 2021-07-23 | P2 | 34.5117326, -119.8202171
Porcelain | 319.1 Data provided by utility does not reflect conditions in the field. | This subject location is identified as 2146670E in the spreadsheet which is different from field observation and is another defect. The severity of the defect of inconsistent information between tracking spreadsheet and field observation (Defect Code: 319.1) is Minor. | WMP3-Grid Design and System Hardening | 2021-02-09 | 2021-04-15 | N/A | 33.8046998, -117.5137319
Porcelain | 318.1 Supply conductor, conductor taps, feeder taps not covered or insulated. | The conductor seems to be exposed which is a defect. The severity of the defect of exposed conductor (Defect code: 318) is Moderate. | WMP3-Grid Design and System Hardening | 2021-02-09 | 2021-03-15 | N/A | 33.8046998, -117.5137319
Cachuma | 510.1 Patrol inspection of vegetation not conducted and documented in addition to Detailed Inspection of vegetation. | Abandoned pole found lying next to SCE pole #43734650E. The severity of this defect is Moderate. | WMP5-Vegetation Management and Inspections | 2021-02-09 | 2021-02-25 | N/A | 34.4760589, -119.7975468
Cachuma | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | The guy wires are touched by vegetation above insulator, which is a defect. The severity of the defect of vegetation touching guywire above insulator (Defect code: 524.1) is Minor. | WMP5-Vegetation Management and Inspections | 2021-02-18 | 2021-09-07 | P2 | 34.4592071, -119.8163141
Cachuma | 515.3 Failure to remove or mitigate all trees with strike potential. | The palm tree is right next to a transformer and below the lowest conductors and the equipment on the cross arm including fuses and transformer without maintaining proper clearance, which is a defect. Many dried palm tree branches need to be removed. The severity of the defect of not maintaining minimum clearance between vegetation and electric line and equipment (Defect code: 515.3) is Minor. | WMP5-Vegetation Management and Inspections | 2021-02-18 | 2021-03-08 | P2 | 34.4593097, -119.8134013
Cachuma | 319.1 Data provided by utility does not reflect conditions in the field. | One conductor is covered and the others remain bare. This is inconsistent with tracking spreadsheet and is a defect. SCE staff will verify the work order and get back to WSD staff of the reason why only top conductor was replaced by covered conductor.Based on discussion with SCE staff on 2/23/2021, these conductors for different circuits will be replaced by covered conductors in the future. The severity of the defect of inconsistent information between tracking spreadsheet and field observation (Defect Code: 319.1) is Minor. | WMP3-Grid Design and System Hardening | 2021-02-18 | 2/18/20221 | N/A | 34.4589512, -119.8195618
Plateau | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | Oak tree in grow-in zone. Oak tree is making contact with Guy wire above insulator in violation of WP5 rule 524.1. Guy wires on the west side of pole. | WMP5-Vegetation Management and Inspections | 2021-03-09 | 2021-09-02 | P2 | 34.0990418, -118.6666842
Tuna | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | Eucalyptus tree near pole is in contact with guy wire triggering violation, Guy wire insulator is below canopy with vegetation contact above guy insulator. 3 eucalyptus trees clear of conductors. | WMP5-Vegetation Management and Inspections | 2021-03-10 | 2021-04-01 | P2 | 34.0443426, -118.6448189
Quarry | 515.3 Failure to remove or mitigate all trees with strike potential. | The palm tree is very close to the conductors above and does not have proper clearance. The severity of the defect of vegetation management is Moderate. | WMP5-Vegetation Management and Inspections | 2021-03-16 | 2021-04-02 | N/A - Handled directly by Veg Mgmt. | 33.94019, -117.5200503
Titus | GO95 1112 Guy wire is loose with no tension. | Defect Code GO95 1112; guy wire is loose with no tension. | GO 95-General Order 95 | 2021-03-18 | 2021-03-18 | P1 | 34.0185668005713, -117.73937474509
Titus | GO95 1113 Anchors supporting wooden pole not visible and is buried under soil. | Defect Code GO95 1113; anchors supporting wooden pole not visible and is buried under soil. This is a non-HFTD area. | GO 95-General Order 95 | 2021-03-18 | 2021-03-18 | Repaired by Inspector | 34.0185668005713, -117.73937474509
Statler | 424.1 Anchors supporting wooden pole not visible or buried under vegetation in HFTD. | Defect code 424.1 guy anchor not visible for pole 4318864E. | WMP4-Asset Management and Inspections | 2021-04-01 | 4/1/20221 | P2 | 33.777087015987, -118.34423469848
Statler | 521.1 Vegetation violates minimum clearance standard (Rule 35, Case 14) in HFTD or PRC 4292 and PRC 4293. | 3 Pepper trees East of pole 2246007E in grow-in zone at .2 span from pole. Vegetation violates minimum clearance standards from conductors. | WMP5-Vegetation Management and Inspections | 2021-04-01 | 2021-04-19 | N/A - Handled directly by Veg Mgmt. | 33.7730191814091, -118.339051609799
Whipstock | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | The guywires above the insulator were touched by vegetation which is a defect. The severity of the defect of vegetation management (Defect code: 524.1) is Moderate. | WMP5-Vegetation Management and Inspections | 2021-04-02 | 2021-06-15 | P2 | 33.9609695164311, -117.950630751254
Whipstock | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | The palm tree leaves touch guywires above the insulator, which is a defect. The severity of the defect of vegetation management (Defect code: 524.1) is Moderate. | WMP5-Vegetation Management and Inspections | 2021-04-02 | 2021-06-15 | P2 | 33.9603559632211, -117.951840916353
Hackberry | 515.3 Failure to remove or mitigate all trees with strike potential. | Bamboos were trimmed down to maintain clearance to the conductors above. Bamboo branches were too close to the conductors and is a defect. The severity of the defect of vegetation management (Defect code: 515.3) is Moderate. | WMP5-Vegetation Management and Inspections | 2021-04-02 | 2021-06-29 | N/A - Handled directly by Veg Mgmt. | 33.9618466090078, -117.957743658867
Palmer | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | Pole 4733123E inspected, vegetation contacting guy wire above guy insulator. Guy wire is at height of secondary. | WMP5-Vegetation Management and Inspections | 2021-04-14 | 2021-04-30 | P2 | 34.1268101253606, -117.750172307683
Lemonade | 524.1 Vegetation contacting guy wire above the guy insulator in HFTD. | Oak tree contacting Guy wire above insulator at pole 669842E. | WMP5-Vegetation Management and Inspections | 2021-04-21 | 2021-06-18 | P2 | 34.1458375775973, -117.832119649077
Lemonade | 424.1 Anchors supporting wooden pole not visible or buried under vegetation in HFTD. | Anchor is buried under vegetation at Pole 669840E. | WMP4-Asset Management and Inspections | 2021-04-21 | 4/21/20221 | P2 | 34.1457652328566, -117.832406212601
1Based upon SCE's maintenance program and within the priority level requirement, this is the planned completion date.
2Pursuant to GO 95, Rule 18, P1 notifications require an immediate action taken by the utility not to exceed 72 hours and P2 Notifications have a 6-month compliance correction period in Tier 3 HFTD and a 1-year period in Tier 2. N/A indicates that the finding does not receive an internal priority classification in SCE's work management system.