## OH_CONDUCTOR_EFF
Feature | Description | relative_importance | scaled_importance | percentage
Avg_Ckt_Pole_Age | Average pole age of all the structures associated to the segment's circuit | 79554.4844 | 1 | 0.053752
LONG_UDF | Segment Longitude, estimated by calculating the mean (center) longitudes of all FLOCs associated to the segment | 68277.9453 | 0.85825 | 0.046133
ICA_GEN_UDF | DERiM ICA Generation value | 66788.3438 | 0.83953 | 0.045126
ICA_LOAD_UDF | DERiM ICA Load value | 57490.2031 | 0.72265 | 0.038844
LAT_UDF | Segment Latitude, estimated by calculating the mean (center) latitudes of all FLOCs associated to the segment | 55246.6602 | 0.69445 | 0.037328
LENGTH_SEG_CAL_TOTAL | Calculated Total Length of segment from the Substation, inclusive of current feature length | 43071.1641 | 0.5414 | 0.029101
CONDUCTOR_SIZE_UDF | Conductor size | 42133.9375 | 0.52962 | 0.028468
EQ_PoleClass | Mode pole class (field in Equipment table: _BIC_ZCAE_P015; values = 1-6, H1-6) of all structures associated to the FLOC | 39820.0039 | 0.50054 | 0.026905
Log_WindForce | Log converstion of downforce | 36660.0781 | 0.46082 | 0.02477
CIRCUIT_KV_UDF | Maximum circuit voltage value | 34445.5508 | 0.43298 | 0.023273
max_wind_magnitude | max wind magnitude | 34009.0547 | 0.42749 | 0.022978
max_cape_lifted_at_surface | maximum Convective Available Potential Energy (CAPE) lifted at the surface | 33819.5625 | 0.42511 | 0.02285
avg_cape_lifted_at_surface | average Convective Available Potential Energy (CAPE) lifted at the surface | 33799.5898 | 0.42486 | 0.022837
max_mixing_ratio_2m | maximum mixing ratio of water vapor at 2 meters above the ground | 33391.875 | 0.41974 | 0.022561
max_surface_downwelling_shortwave_flux | maximum amount of shortwave radiation (sunlight) that reaches the Earth’s surface | 33305.7617 | 0.41865 | 0.022503
sum_hourly_precipitation_amount | 1 Hour Rainfall Intervals | 32577.1484 | 0.40949 | 0.022011
avg_wind_magnitude | average wind magnitude | 31685.5547 | 0.39829 | 0.021409
atmospheric_corrosivity | Atmospheric corrosivity intensity (1-5) | 31578.3867 | 0.39694 | 0.021336
avg_air_temperature | average Air Temperature | 31093.4375 | 0.39084 | 0.021009
Conductor_AGE_UDF | Conductor age, calculated by referring to IN_SERVICE_DATE from GE Smallworld and imputing missing values using age of structures on the circuit | 31003.2559 | 0.38971 | 0.020948

## OH_CONDUCTOR_CFO
Feature | Description | relative_importance | scaled_importance | percentage
DOWNSTREAM_KVA | Downstream Total KVA count found at the end of conductor, exclusive of the current conductor kva | 886688.0625 | 1 | 0.040969
EQ_PoleClass | Mode pole class (field in Equipment table: _BIC_ZCAE_P015; values = 1-6, H1-6) of all structures associated to the FLOC | 751802.5 | 0.84788 | 0.034737
CONDUCTOR_SIZE_UDF | Conductor size | 637702.75 | 0.7192 | 0.029465
IS_AUTOMATED | Indicate type of switch found at the START of the conductor values are null no switch, 1=normal switch, 2=remote switch , 3=automated switch, 4=automated and remote switch | 629350.5625 | 0.70978 | 0.029079
EQ_PoleHeight | Average pole height of all structures associated to the FLOC | 556123.375 | 0.62719 | 0.025696
DOWNSTREAM_O_CUST | OTHER Downstream Total Customer count | 531125.9375 | 0.599 | 0.024541
Mean_Pole_Age | Average pole age of all the structures associated to the segment's circuit | 529381.375 | 0.59703 | 0.02446
LAT_UDF | Segment Latitude, estimated by calculating the mean (center) latitudes of all FLOCs associated to the segment | 526714.9375 | 0.59403 | 0.024337
DOWNSTREAM_CUST | Downstream Total Customer count found at the end of the conductor, exclusive of current conductor customer count. When no serial number match for a transformer, default to 1 customer | 518489.1875 | 0.58475 | 0.023957
AVIAN_2017 | Avian incidents 2017 | 512405.5625 | 0.57789 | 0.023676
LONG_UDF | Segment Longitude, estimated by calculating the mean (center) longitudes of all FLOCs associated to the segment | 507393.625 | 0.57223 | 0.023444
FARS_ALL_YEARS | Kernel density estimate for yearly vehicle accidents within a grid where the segment locates | 501709.8125 | 0.56582 | 0.023182
max_cape_lifted_at_surface | maximum Convective Available Potential Energy (CAPE) lifted at the surface | 496565.2812 | 0.56002 | 0.022944
avg_air_temperature | average Air Temperature | 487932.875 | 0.55029 | 0.022545
Switch_Counts | Number of switch transactions on the circuit associated to the segment | 482821.8125 | 0.54452 | 0.022309
DOWNSTREAM_R_CUST | RESIDENTIAL Downstream Total Customer count | 481360.8438 | 0.54288 | 0.022241
AVIAN_2020 | Avian incidents 2020 | 472235.875 | 0.53258 | 0.02182
max_shortwave_downwelling_shortwave_flux | maximum amount of shortwave radiation (sunlight) that reaches the Earth’s surface | 457199.9375 | 0.51563 | 0.021125
avg_cape_lifted_at_surface | average Convective Available Potential Energy (CAPE) lifted at the surface | 447610 | 0.50481 | 0.020682
sum_hourly_precipitation_amount | 1 Hour Rainfall Intervals | 441593.0625 | 0.49803 | 0.020404

## TRANSMISSION_EFF
Variable | Description | relative_importance
Imminent_Contact_clearance_bucket_trees | Tree is touching or close to touching wire | 0.034713
EQ_CatalogProfile | Equipment Catalog Profile associated to FLOC | 0.032675
std_surface_downwelling_shortwave_flux | standard deviation of surface downwelling shortwave flux, which refers to the amount of solar radiation reaching the Earth's surface. | 0.029078
EQ_SubType | Equipment Subtype associated to FLOC | 0.027071
EQ_SystemVoltage | Equipment System Voltage associated to FLOC | 0.024659
FLOC_Latitude | Latitude of FLOC | 0.022141
FLOC_Longitude | Longitude of FLOC | 0.021942
std_mixing_ratio_2m | standard deviation of the mixing ratio, which is a measure of the amount of water vapor in the air--typically expressed in grams of water vapor per kilogram of dry air. | 0.020556
DaysInService | Number of days between date at start of model year and the structure in service date | 0.01909
sum(hourly_precipitation_amount) | 1 Hour Rainfall Intervals | 0.018498
stddev_cape_max_lifted_between_850mb_700mb | CAPE is a measure of the amount of energy available for convection, which is crucial for understanding the potential for thunderstorms and severe weather. standard deviation of CAPE maximized between the pressure levels of 850 millibars (mb) and 700 millibars (mb). | 0.018387
avg(mid_cloud_fraction) | average mid cloud coverage | 0.018271
stddev_cape_lifted_at_surface | standard deviation of Convective Available Potential Energy (CAPE) lifted at the surface | 0.018236
avg_mixing_ratio_2m | average mixing ratio of water vapor at 2 meters above the ground | 0.018118
sum(hourly_snow_water_equivalent) | 1 Hour Snowfall | 0.017736
stddev_pop(mid_cloud_fraction) | Measures the variability or dispersion of mid cloud fraction values within a population. | 0.017704
n_hours_temp_lt36 | number of hours during which the air temperature was less than 36°F. | 0.017689
n_hours_temp_gt100 | number of hours during which the air temperature was greater than 100°F. | 0.017628
avg_surface_downwelling_shortwave_flux | average amount of shortwave radiation (sunlight) that reaches the Earth’s surface | 0.01759
stddev_pop(high_cloud_fraction) | Measures the variability or dispersion of high cloud fraction values within a population. | 0.017561

## TRANSMISSION_CFO
Variable | Description | relative_importance
EQ_CatalogProfile | Equipment Catalog Profile associated to FLOC | 0.032059
RCD_clearance_bucket_trees | Regulation Clearance Distance | 0.031006
FLOC_Longitude | Longitude of FLOC | 0.02643
Imminent_Contact_clearance_bucket_trees | Tree is touching or close to touching wire | 0.025113
EQ_SubType | Equipment Subtype associated to FLOC | 0.023634
FLOC_Latitude | Latitude of FLOC | 0.022298
std_surface_downwelling_shortwave_flux | standard deviation of surface downwelling shortwave flux, which refers to the amount of solar radiation reaching the Earth's surface. | 0.020755
TCD_clearance_bucket_trees | Trigger Clearance Distance | 0.020021
EQ_SystemVoltage | Equipment System Voltage associated to FLOC | 0.017997
avg_cape_lifted_at_surface | average Convective Available Potential Energy (CAPE) lifted at the surface | 0.017394
std_mixing_ratio_2m | standard deviation of the mixing ratio, which is a measure of the amount of water vapor in the air -- typically expressed in grams of water vapor per kilogram of dry air. | 0.017209
sum_hourly_snow_water_equivalent | 1 Hour Snowfall | 0.016808
stddev_cape_max_lifted_between_850mb_700mb | CAPE is a measure of the amount of energy available for convection, which is crucial for understanding the potential for thunderstorms and severe weather. standard deviation of CAPE maximized between the pressure levels of 850 millibars (mb) and 700 millibars (mb). | 0.016658
DaysInService | Number of days between date at start of model year and the structure in service date | 0.015297
sum(hourly_precipitation_amount) | 1 Hour Rainfall Intervals | 0.015296
stddev_pop_soil_temperature_level_1 | standard deviation Soil Temperature at 0-10cm | 0.015219
avg_soil_temperature_level_1 | average Soil Temperature at 0-10cm | 0.015179
avg_surface_downwelling_shortwave_flux | average amount of shortwave radiation (sunlight) that reaches the Earth’s surface | 0.015082
n_hours_temp_gt100 | number of hours during which the air temperature was greater than 100°F. | 0.014893
avg_wind_magnitude | average wind magnitude | 0.014872

## TRANSFORMER
variable | Description | relative_importance | scaled_importance | percentage
AGE_UDF | Transformer age, calculated by referring to IN_SERVICE_DATE and Start_Up_Date | 1.0868 | 1 | 19.9596
CLIMATECODE_UDF | The California Energy Commission (CEC) has established 16 geographic climate zones based on energy use, temperature, weather and other factors. Each California ZIP Code is assigned to one of the climate zones. | 1.0867 | 0.99992 | 19.9581
Peak_Loading | Peak Loading of XFMR using nameplate | 0.27105 | 0.24941 | 4.9781
Percent_Time_Overloaded | Percent of time XFMR had overloading according to nameplate | 0.25561 | 0.2352 | 4.6945
KVA_UDF | KVA size of transformers | 0.16539 | 0.15219 | 3.0376
FLD_ZONE_X | Is in Flood Zone X | 0.12185 | 0.11212 | 2.2379
OHUGInd_UDF_OH | Indicates if the FLOC is OH | 0.10827 | 0.099628 | 1.9885
PRIMARY_RATING | Voltage Rating | 0.083813 | 0.077122 | 1.5393
FINAL_SCD | Short Circuit Duty. Represents amount of fault current at that location | 0.062112 | 0.057154 | 1.1408
REGION_UDF_SanJoaquin | Is in the San Joaquin region | 0.054592 | 0.050234 | 1.0027
Subtype_BD-BURD | Has subtype BURD | 0.045283 | 0.041668 | 0.83168
OHUGInd_UDF_UG | Indicates if the FLOC is UG | 0.044361 | 0.040819 | 0.81474
REGION_UDF_MetroWest | Is in the Metro West region | 0.044157 | 0.040632 | 0.811
REGION_UDF_MetroEast | Is in the Metro East region | 0.043663 | 0.040177 | 0.80192
REGION_UDF_NCoast | Is in the North Coast region | 0.043077 | 0.039638 | 0.79117
REGION_UDF_SanJacinto | Is in the San Jacinto region | 0.042259 | 0.038886 | 0.77615
avg_soil_moisture_level_1 | Avg Soil Moisture at 0-10cm | 0.041143 | 0.037858 | 0.75563
FLD_ZONE_D | Is in Flood Zone D | 0.041088 | 0.037808 | 0.75463
LoadingRatio | if Average_Loading is missing, LoadingRatio is set to 0. Otherwise, it calculates the ratio of Peak_Loading to Average_Loading. | 0.040675 | 0.037428 | 0.74704
Model_GROUP_Group0 | Is in Model group 0 | 0.039353 | 0.036211 | 0.72276

## CAPACITOR
Variable | Description | relative_importance
FLOC_StructureType | the structure type as defined by the floc table (ed pole, ed vault, ed pad, etc) | 0.038765
n_hours_temp_gt100 | number of hours during which the air temperature was greater than 100°F. | 0.036643
InServiceAge | Equipment age, calculated by subtracting the equipment's startup date (EQ_StartUpDate) from January 1, 2024 | 0.032642
PLL | Planned Loading Limit | 0.031233
EQ_SwitchType | Equipment Switch Type | 0.028527
avg_mixing_ratio_2m | average mixing ratio of water vapor at 2 meters above the ground | 0.025961
avg_surface_downwelling_shortwave_flux | average amount of shortwave radiation (sunlight) that reaches the Earth’s surface | 0.025643
N_hours_windgust_gt46 | number of hours with wind gusts greater than 46 mph | 0.025594
avg(low_cloud_fraction) | average low cloud coverage | 0.025335
percent_of_time_cap_test_pass | automated test variable, capacitors are tested every day automaticaly and this quantifies how often the test passes | 0.025256
Structure_StartUpYear | Parsed from SAP EQ_StartUpDate, engineers identified that there were certain design standards that were changed in certain years. | 0.024564
avg_cape_lifted_at_surface | average Convective Available Potential Energy (CAPE) lifted at the surface | 0.023727
avg(accumulated_snow_melt) | average amount of snow that has melted in kg | 0.023664
avg(snow_depth) | average snow depth | 0.023459
EQ_SubType | Equipment Subtype associated to FLOC | 0.023406
avg_mvar_delta | average change in MegaVolt Ampere Reactive (MVAR) readings | 0.023302
SUM_of_SAIDI | Reliability indices SAIDI, SAIFI, and MAIFI are summed to the circuit, for a year, then averaged over 5 years to get an average yearly circuit reliability which is applied to appropriate cables based on what circuits they are attached to | 0.023179
EQ_OhOrUg | Indicates if Equipment is Overhead or Underground | 0.021859
N_hours_sustwind_gt30 | number of hours with sustained wind speeds greater than 30 mph | 0.021691
sum_hourly_precipitation_amount | 1 Hour Rainfall Intervals | 0.021465

## OH_AUTO_SWITCH
Feature | Description | relative_importance | scaled_importance | percentage
manufacturer_UDF | Manufacturer of the switch | 62344.9336 | 1 | 0.21783
AGE_UDF | Calculated age of switch equipment | 30144.8867 | 0.48352 | 0.10532
region_UDF | Region where the switch resides | 20728.916 | 0.33249 | 0.072425
oms_switching_cts | Counted # of times the switch was operated. An operation is either open or close. | 16290.4883 | 0.2613 | 0.056917
DOWNSTREAM_KVA | Downstream kVA. Represents capacity | 10815.7637 | 0.17348 | 0.037789
eq_sys_voltage_UDF | Voltage handled by the equipment | 8530.7207 | 0.13683 | 0.029806
avg_wind_magnitude | average wind magnitude | 5553.6182 | 0.089079 | 0.019404
max_hourly_precipitation_amount | maximum 1 hour rainfall intervals | 5479.3643 | 0.087888 | 0.019144
max_cape_max_lifted_between_850mb_700mb | CAPE is a measure of the amount of energy available for convection, which is crucial for understanding the potential for thunderstorms and severe weather. maximum CAPE maximized between the pressure levels of 850 millibars (mb) and 700 millibars (mb). | 5450.1328 | 0.087419 | 0.019042
avg_mid_cloud_fraction | average mid cloud coverage | 5444.1494 | 0.087323 | 0.019021
SCD | Short Circuit Duty. Represents amount of fault current at that location | 5353.1279 | 0.085863 | 0.018703
avg_surface_wind_gust | average surface wind gust | 5342.4736 | 0.085692 | 0.018666
avg_cape_max_lifted_between_850mb_700mb | average Convective Available Potential Energy (CAPE) maximized between the pressure levels of 850 millibars (mb) and 700 millibars (mb). | 5330.2017 | 0.085495 | 0.018623
n_hours_temp_gt100 | number of hours during which the air temperature was greater than 100°F. | 5175.7744 | 0.083018 | 0.018084
ASSET_SUBTYPE_UDF | Switch asset subtype (Accessory or Pole Disconnect, Dip, Horizontal, Tiered, Triangular, Vertical) | 5051.9712 | 0.081033 | 0.017651
max_mixing_ratio_2m | maximum mixing ratio of water vapor at 2 meters above the ground | 4968.8828 | 0.0797 | 0.017361
max_wind_magnitude | maximum wind magnitude | 4729.271 | 0.075857 | 0.016524
avg_high_cloud_fraction | average high cloud coverage | 4705.2378 | 0.075471 | 0.01644
max_cape_lifted_at_surface | maximum Convective Available Potential Energy (CAPE) lifted at the surface | 4600.1504 | 0.073785 | 0.016072
max_surface_wind_gust | maximum of surface wind gusts | 4532.6885 | 0.072703 | 0.015837