## SCE Approved
Manufacturer Name | Approved Model Number1 | Approved Mode For Notification Only Projects |  | Type of Equipment | Additional Required PCS Devices | Current Measurement Reference Points | Description | UL 1741 Power Control Systems (PCS) Certification Requirement Decision (CRD) |  | UL 1741 PCS - ESS Operating Modes |  | Max Open Loop Response Time |  | Single/Multi Phase | Output Voltage | Maximum Continuous Current | Maximum Continuous Power | Notes | PCS Information Listing Date | Last Update | Field Verified?
|  | Import Only | No Exchange | Inverter or ESS |  |  |  | Issuing Entity | Document Date (mo/day/yr) | Import Only Mode | No Exchange Mode | Import Only Mode (Seconds) | No Exchange Mode (Seconds) |  | (V) | (A) | (kVA) |  | (mm/dd/yyyy) | (mm/dd/yyyy)
Tesla Inc. | AC Powerwall 1092170-xx-y | Y | N | ESS | Tesla Gateway 1 (1118431-xx-y) or Tesla Gateway 2 (1232100-xx-y) | Whole home back-up mode: Tesla Gateway Partial back-up mode: External CT | Energy Storage System paired with Tesla Gateway for PCS functionality | Intertek | 2020-05-20 | Y | N | 1.96* | N/A | Single | 240 | 200 | 58 | *1.96 seconds is applicable when used with Tesla Gateway 1 (1118431-xx-y). 1.76 seconds is applicable when used with Tesla Gateway 2 (1232100-xx-y). | 2021-02-22 |  | Yes
Tesla Inc. | AC Powerwall 2012170-xx-y | Y | N | ESS | Tesla Gateway 1 (1118431-xx-y) or Tesla Gateway 2 (1232100-xx-y) | Whole home back-up mode: Tesla Gateway Partial back-up mode: External CT | Energy Storage System paired with Tesla Gateway for PCS functionality | Intertek | 2020-05-20 | Y | N | 1.96* | N/A | Single | 240 | 200 | 58 | *1.96 seconds is applicable when used with Tesla Gateway 1 (1118431-xx-y). 1.76 seconds is applicable when used with Tesla Gateway 2 (1232100-xx-y). | 2021-02-22 |  | Yes
Tesla Inc. | AC Powerwall 3012170-xx-y | Y | N | ESS | Tesla Gateway 2 (1232100-xx-y) | Whole home back-up mode: Tesla Gateway Partial back-up mode: External CT | Energy Storage System paired with Tesla Gateway for PCS functionality | Intertek | 2020-11-13 | Y | N | 1.76 | N/A | Single | 240 | 200 | 58 |  | 2021-05-11 |  | Yes

## Full Approved List of PCS
Manufacturer Name | Approved Model Number1 | Approved Mode For Notification Only Projects |  | Type of Equipment | Additional Required PCS Devices | Current Measurement Reference Points | Description | UL 1741 Power Control Systems (PCS) Certification Requirement Decision (CRD) |  | UL 1741 PCS - ESS Operating Modes |  | Max Open Loop Response Time |  | Single/Multi Phase | Output Voltage | Maximum Continuous Current | Maximum Continuous Power | Notes | PCS Information Listing Date | Last Update | SCE Field Verified?
|  | Import Only | No Exchange | Inverter or ESS |  |  |  | Issuing Entity | Document Date (mo/day/yr) | Import Only Mode | No Exchange Mode | Import Only Mode (Seconds) | No Exchange Mode (Seconds) |  | (V) | (A) | (kVA) |  | (mm/dd/yyyy) | (mm/dd/yyyy)
Tesla Inc. | AC Powerwall 1092170-xx-y | Y | N | ESS | Tesla Gateway 1 (1118431-xx-y) or Tesla Gateway 2 (1232100-xx-y) | Whole home back-up mode: Tesla Gateway Partial back-up mode: External CT | Energy Storage System paired with Tesla Gateway for PCS functionality | Intertek | 2020-05-20 | Y | N | 1.96* | N/A | Single | 240 | 200 | 58 | *1.96 seconds is applicable when used with Tesla Gateway 1 (1118431-xx-y). 1.76 seconds is applicable when used with Tesla Gateway 2 (1232100-xx-y). | 2021-02-22 |  | Yes
Tesla Inc. | AC Powerwall 2012170-xx-y | Y | N | ESS | Tesla Gateway 1 (1118431-xx-y) or Tesla Gateway 2 (1232100-xx-y) | Whole home back-up mode: Tesla Gateway Partial back-up mode: External CT | Energy Storage System paired with Tesla Gateway for PCS functionality | Intertek | 2020-05-20 | Y | N | 1.96* | N/A | Single | 240 | 200 | 58 | *1.96 seconds is applicable when used with Tesla Gateway 1 (1118431-xx-y). 1.76 seconds is applicable when used with Tesla Gateway 2 (1232100-xx-y). | 2021-02-22 |  | Yes
Tesla Inc. | AC Powerwall 3012170-xx-y | Y | N | ESS | Tesla Gateway 2 (1232100-xx-y) | Whole home back-up mode: Tesla Gateway Partial back-up mode: External CT | Energy Storage System paired with Tesla Gateway for PCS functionality | Intertek | 2020-11-13 | Y | N | 1.76 | N/A | Single | 240 | 200 | 58 |  | 2021-05-11 |  | Yes
Generac Power Systems | X7602 [240V] | Y | Y | Inverter | ESS-tied system: PWRcell battery cabinet Total home monitoring: Neurio PN 011.00021B.F | PV only: Inverter PV + ESS: Inverter & PWRcell battery Total home monitoring PV only: Inverter & Additional Neurio PN 011.00021B.F Total home monitoring PV + ESS: Inverter & PWRcell battery & Additional Neurio PN 011.00021B.F | Inverter with PCS functionality, may be installed in various PCS configurations. Compatible with Generac PWRcell ESS equipment. | Intertek | 2020-12-01 | Y | Y | 1.2 | 1.2 | Single | 240 | 32 | 7.6 |  | 2020-12-11 |  | No
Generac Power Systems | XVT076A03 [240V] | Y | Y | Inverter | ESS-tied system: PWRcell battery cabinet Total home monitoring: Neurio PN 011.00021B.F | PV only: Inverter PV + ESS: Inverter & PWRcell battery Total home monitoring PV only: Inverter & Additional Neurio PN 011.00021B.F Total home monitoring PV + ESS: Inverter & PWRcell battery & Additional Neurio PN 011.00021B.F | Inverter with PCS functionality, may be installed in various PCS configurations. Compatible with Generac PWRcell ESS equipment. | Intertek | 2020-12-01 | Y | Y | 1.2 | 1.2 | Single | 240 | 32 | 7.6 |  | 2020-12-11 |  | No
Generac Power Systems | X11402 [208V] | Y | Y | Inverter | ESS-tied system: PWRcell battery cabinet Total home monitoring: Neurio PN 011.00021B.F | PV only: Inverter PV + ESS: Inverter & PWRcell battery Total home monitoring PV only: Inverter & Additional Neurio PN 011.00021B.F Total home monitoring PV + ESS: Inverter & PWRcell battery & Additional Neurio PN 011.00021B.F | Inverter with PCS functionality, may be installed in various PCS configurations. Compatible with Generac PWRcell ESS equipment. | Intertek | 2020-12-01 | Y | Y | 1.2 | 1.2 | Multi | 208 | 32 | 11.4 |  | 2020-12-11 |  | No
Generac Power Systems | XVT114G03 [208V] | Y | Y | Inverter | ESS-tied system: PWRcell battery cabinet Total home monitoring: Neurio PN 011.00021B.F | PV only: Inverter PV + ESS: Inverter & PWRcell battery Total home monitoring PV only: Inverter & Additional Neurio PN 011.00021B.F Total home monitoring PV + ESS: Inverter & PWRcell battery & Additional Neurio PN 011.00021B.F | Inverter with PCS functionality, may be installed in various PCS configurations. Compatible with Generac PWRcell ESS equipment. | Intertek | 2020-12-01 | Y | Y | 1.2 | 1.2 | Multi | 208 | 32 | 11.4 |  | 2020-12-11 |  | No
OutBack Power Technologies, Inc. | GS4048A [240V] | Y | Y | Inverter | No Information Submitted | Inverter | Inverter with PCS functionality | Intertek | 2020-11-20 | Y | Y | 1.2 | 0.4 | Single | 240 | 15 | 3.6 |  | 2020-12-01 |  | No
OutBack Power Technologies, Inc. | SBX5048-120/240 [240V] | N | Y | Inverter | No Information Submitted | Inverter | Inverter with PCS functionality | Intertek | 2020-10-19 | Y | Y | 13.6 | 0.4 | Single | 240 | 24 | 5 |  | 2020-12-21 |  | No
OutBack Power Technologies, Inc. | GS8048A [240V] | Y | Y | Inverter | No Information Submitted | Inverter | Inverter with PCS functionality | Intertek | 2020-11-20 | Y | Y | 1.2 | 0.4 | Single | 240 | 30 | 7.2 |  | 2020-12-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 8200TL-XH-US [208V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Multi | 208 | 35 | 8.2 |  | 2021-04-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 8200TL-XH-US [240V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Single | 240 | 35 | 8.2 |  | 2021-04-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 9000TL-XH-US [208V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Multi | 208 | 38 | 9 |  | 2021-04-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 9000TL-XH-US [240V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Single | 240 | 38 | 9 |  | 2021-04-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 10000TL-XH-US [208V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Multi | 208 | 42 | 10 |  | 2021-04-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 10000TL-XH-US [240V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Single | 240 | 42 | 10 |  | 2021-04-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 11400TL-XH-US [208V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Multi | 208 | 48 | 11.4 |  | 2021-04-01 |  | No
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 11400TL-XH-US [240V] | Y | N | Inverter | Growatt SM-US-200 Meter | Inverter & External CT | Inverter with PCS functionality | Intertek | 2021-02-03 | Y | Y | 0.8 | 11..4 | Single | 240 | 48 | 11.4 |  | 2021-04-01 |  | No
Tesla Inc. | 1462965-XX-Y [480V, 2hr] | Y | N | ESS | Tesla Site Controller & Accuenergy Acuvim II Meter & compatible CTs | Accuenergy Acuvim II Meter & compatible CTs | Energy Storage System paired with Tesla Site Controller for PCS functionality, may be paired with PV system | Intertek | 44155 | Y | N | 1.764 | N/A | Multi | 480 | 24000 | 20000 | The Megapack System scales up to 2.5 MWh+. A single 2 hour Megapack can consist from 1 to 22 inverters and from 1 to 15 battery pods. Maximum continuous current and power are based on the largest scalable configuration of Megapack. | 2021-01-21 |  | No
Tesla Inc. | 1462965-XX-Y [480V, 4hr] | Y | N | ESS | Tesla Site Controller & Accuenergy Acuvim II Meter & compatible CTs | Accuenergy Acuvim II Meter & compatible CTs | Energy Storage System paired with Tesla Site Controller for PCS functionality, may be paired with PV system | Intertek | 44155 | Y | N | 1.764 | N/A | Multi | 480 | 24000 | 20000 | The Megapack System scales up to 2.5 MWh+. A single 4 hour Megapack can consist from 1 to 22 inverters and from 1 to 17 battery pods. Maximum continuous current and power are based on the largest scalable configuration of Megapack. | 2021-01-21 |  | No
Tesla Inc. | 1462965-XX-Y [505V, 2hr] | Y | N | ESS | Tesla Site Controller & Accuenergy Acuvim II Meter & compatible CTs | Accuenergy Acuvim II Meter & compatible CTs | Energy Storage System paired with Tesla Site Controller for PCS functionality, may be paired with PV system | Intertek | 44155 | Y | N | 1.764 | N/A | Multi | 505 | 24000 | 20000 | The Megapack System scales up to 2.5 MWh+. A single 2 hour Megapack can consist from 1 to 22 inverters and from 1 to 15 battery pods. Maximum continuous current and power are based on the largest scalable configuration of Megapack. | 2021-01-21 |  | No
Tesla Inc. | 1462965-XX-Y [505V, 4hr] | Y | N | ESS | Tesla Site Controller & Accuenergy Acuvim II Meter & compatible CTs | Accuenergy Acuvim II Meter & compatible CTs | Energy Storage System paired with Tesla Site Controller for PCS functionality, may be paired with PV system | Intertek | 44155 | Y | N | 1.764 | N/A | Multi | 505 | 24000 | 20000 | The Megapack System scales up to 2.5 MWh+. A single 4 hour Megapack can consist from 1 to 22 inverters and from 1 to 17 battery pods. Maximum continuous current and power are based on the largest scalable configuration of Megapack. | 2021-01-21 |  | No
Tesla Inc. | Powerpack 2 system [2hr] | Y | N | ESS | Tesla Site Controller & Accuenergy Acuvim II Meter & compatible CTs | Accuenergy Acuvim II Meter & compatible CTs | Energy Storage System paired with Tesla Site Controller for PCS functionality, may be paired with PV system | Intertek | 44155 | Y | N | 1.764 | N/A | Multi | 480 | 24000 | 20000 | The Powerpack System scales from 100 kWh+ to 100 MWh+. A single Powerpack can consist from 1 to 10 inverters and from 1 to 20 battery pods. Maximum continuous current and power are based on the largest scalable configuration of Powerpack. | 2020-12-21 |  | No
Tesla Inc. | Powerpack 2 system [4hr] | Y | N | ESS | Tesla Site Controller & Accuenergy Acuvim II Meter & compatible CTs | Accuenergy Acuvim II Meter & compatible CTs | Energy Storage System paired with Tesla Site Controller for PCS functionality, may be paired with PV system | Intertek | 44155 | Y | N | 1.764 | N/A | Multi | 480 | 24000 | 20000 | The Powerpack System scales from 100 kWh+ to 100 MWh+. A single Powerpack can consist from 1 to 10 inverters and from 1 to 20 battery pods. Maximum continuous current and power are based on the largest scalable configuration of Powerpack. | 2020-12-21 |  | No