## Slide 1: SCE’s Interim Methodology for Assessing Contribution to RNUs
SCE’s methodology will be implemented on an interim basis to assess whether a proposed Generating Facility is not reasonably anticipated to require or contribute to the need for Reliability Network Upgrades (RNU).
The assessment will consist of Flow Impact, Short Circuit Duty, Transient Stability, and Reactive Support tests.
If the current Cluster Study base case is unavailable, the latest completed Cluster Study base case will be used.
The Generating Facility shall pass the Flow Impact Test if the following three criteria are met:
  (i) The Generating Facility’s size, in aggregate with earlier queued Generating Facilities currently being studied through the Independent Study Process (ISP), is 5% or less of the capacity of:
    1) the nearest transmission line; or
    2) transformer which has a high-side transmission voltage.
    If multiple transmission lines or transformers are the same electrical distance away from the Generating
    Facility, the 5% will be based on the facility with the lowest normal rating.
  (ii) The incremental power flow should not increase the percent loading on the highest loaded transmission facility up to one substation away past 99% loading.
  (iii) The incremental power flow should not increase the percent loading of any transmission facility in the Cluster Study Subarea past 99.9%.
  If an earlier queued study hasn’t yet determined if RNUs are needed, the new assessment will wait for those results.
Distribution
Substation
CAISO
Substation
Gen
Facility
Distribution
Line
CAISO Line #1
83 MVA
CAISO Line #2
124 MVA
Perform Test on this facility
Example 1)
Gen
Facility
CAISO Line #1
CAISO Line #2
XFMR #1
308 MVA
XFMR #2
280 MVA
Perform Test on this facility
Example 2)
Red = CAISO Facility
Black = Distribution Facility

## Slide 2
Short Circuit Duty Test
The Generating Facility shall pass the short circuit test if (i) the combined short circuit contribution from all the active Interconnection Requests in the Independent Study Process in the same study area is less than five (5) percent of the available capacity of the latest circuit breaker upgrade and; (ii) total fault duty on each circuit breaker upgrade identified for the latest Queue Cluster and active Independent Study Process Interconnection Requests in the same study area is less than ninety-five (95) percent of the nameplate capacity of the respective circuit breaker upgrade.
Transient Stability Test
The Generating Facility shall pass the transient stability test if the Generating Facility has requested interconnection in a study area where transient stability issues are not identified for active Interconnection Requests in the latest Queue Cluster or Independent Study Process.
Reactive Support Test
The Generating Facility shall pass the reactive support test if the Generating Facility has requested interconnection in a study area where reactive support needs are not identified as requiring Reliability Network Upgrades for active Interconnection Requests in the latest Queue Cluster or Independent Study Process.
SCE’s Interim Methodology for Assessing Contribution to RNUs
(Continued)